## HEALTH AND SAFETY
SCHEDULE OF QUANTITIES: HEALTH AND SAFETY
WITS UNIVERSITY - WEST CAMPUS ¦STURROCK PARK ¦ MARKS PARK ¦ BREDNOR HOUSE ¦ KNOCKANDO ¦ STERKFONTEIN
BILLS OF QUANTITIES |  |  | SCHEDULE 1: HEALTH AND SAFETY
All rates to be VAT Exclusive
PAYMENT REFERS | ITEM NO | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
| 1.0 | HEALTH AND SAFETY
| 1.1 | Prepare a Health and Safety File including proof of registration and Good Standing with the compensation fund and submit to management | Sum | 1
Total carried forward to summary 1

## INSPECTION
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
All rates to be VAT Exclusive
BILL 2
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
FIRE FIGHTING EQUIPMENT
(Initial inspection for benchmarking and establishing immediate maintenance needs. Rate in this section to include inspection labour, travel and reporting related needs)
2 | WEST CAMPUS
2.1 | Intial Inspection and reporting on existing installations
2,1,1 | Fire hydrants | No. | 365
2,1,2 | Fire hose reels | No. | 996.6
2,1,3 | Fire extinguishers - 4.5kg DCP Type | No. | 1131.9
2,1,4 | Fire extinguishers - 9kg DCP Type | No. | 1623.6
2,1,5 | Fire extinguishers - 5kg CO2 Type | No. | 627
2,1,6 | Fire extinguishers - 2,5kg CO2 Type | No. | 361.9
2,1,7 | Booster Connection | No. | 7
2,1,8 | Water Storage Tank | No. | 2
2.2 | Sprinkler Systems
2,2,1 | Complete building with Sprinkler System | No. | 7
Carried to final summary 2

## YEARLY SERVICING
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
All rates to be VAT Exclusive
BILL 3
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
FIRE FIGHTING EQUIPMENT
Pricing in this section to comprise of all inclusive rates with the scope as specified and also factoring in any other specific manufacturer requirements. The callout fees, traveling, labour, consumables and any parts that may be required must be included in the rates provided.
3 | WEST CAMPUS
3.1 | Service existing fire-fighting equipment yearly
3,1,1 | Fire hydrants | No. | 365
3,1,2 | Fire hose reels | No. | 996.6
3,1,3 | Fire extinguishers - 4.5kg DCP Type | No. | 1131.9
3,1,4 | Fire extinguishers - 9kg DCP Type | No. | 1623.6
3,1,5 | Fire extinguishers - 5kg CO2 Type | No. | 627
3,1,6 | Fire extinguishers - 2,5kg CO2 Type | No. | 361.9
3,1,7 | Booster Connection | No. | 7
3,1,8 | Water Storage Tank | No. | 2
3.2 | Servicing and repairing fire pumps
3,2,1 | Service 50 kW electric driven Mather | No. | 1
and Platt pump
3,2,2 | Service 50 kW diesel driven Mather | No. | 1
and Platt pump (Pump only)
3,2,3 | Service 20 kW electric driven Mather | No. | 1
and Platt pump.
3,2,4 | Service 200 mm Non-Return valve | No. | 2
3,2,5 | Service 150 mm gate valve | No. | 2
3,2,6 | Service 150 mm Non Return valve | No. | 2
3,2,7 | Service 200 mm Non-Return valve | No. | 2
3,3 | Servicing and repairing Sprinkler System (once per
month per building for 7 buildings)
3,3,1 | Butterfly Valves
3,3,1,1 | Check valves are open and secured with a chain | No. | 84
3,3,1,2 | Record pressure on the supply chain mains before test | No. | 84
3,3,1,3 | Record the pressure on the sprinkler before test | No. | 84
3,3,2 | Sprinklers and Piping
3,3,2,1 | Check all external pipe work that is in the area of the sprinkler | Item | 84
valve chambers and canopies and report findings.
3,3,2,2 | Check all internal pipe work in the sprinkler valve chamber | Item | 84
and report findings.
3,3,2,3 | Partly open the terminal drain valve and let the water run | No. | 84
until the alarm gong activates.
3,3,3 | Alarm Valves
3,3,3,1 | Check system pressure gauges and record pressure | No. | 84
readings on completion of the test on the sprinkler installations
3,3,3,2 | Check manifold pressure gauge and record pressure | No. | 84
reading on completion of test.
3,3,3,3 | Check valve trim pipe work installation and report any | No. | 84
damages, leaks and non-compliances.
3,3,3,4 | Check operation of water motor and gong for seconds and | No. | 468
report any non compliances. Record how long it takes the
for the gong to ring.
3,3,4 | Fire Alarm Monitoring
3,3,4,1 | Check flow switch operation | No. | 84
3,3,4,2 | Check that closing isolating valve will change state | No. | 84
of potential free contact.
'3,4 | Update as built information and operating and maintenance manual | Set | 3
Carried to final summary 3 |  |  |  |  | 0

## CORRECTIVE MAINTENANCE YR 1
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
CALL OUT RATES
BILL 4 - YEAR 1
All rates to be VAT Exclusive
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
4 | STAFF RATES
Corrective Maintenance
4.1.1 | Technician (Office Hours) | Hr | 120
4.1.2 | Technician (After Hours) | Hr | 80
4.1.3 | Artisan (Office Hours) | Hr | 120
4.1.4 | Artisan (After Hours) | Hr | 80
4.2 | Call Outs (Including travelling)
4.2.1 | Call out - Office Hours | No. | 30
4.2.2 | Call out - After Hours | No. | 20
4.3 | Spares Mark Up (for evaluation R1000000)
4.3.1 | less than R20 000 | sum
4.3.2 | Contractor's Mark Up | % |  | 20000
4.3.3 | 20001 to R50000 | sum | - | -
4.3.4 | Contractor's Mark Up | % |  | 50000
4.3.5 | more than R50000 | sum
4.3.6 | Contractor's Mark Up | % | 0 | 830000
4.4 | Replace Fire Extinguishers
4.4.1 | Fire extinguishers - 4.5kg DCP Type | No. | 48
4.4.2 | Fire extinguishers - 9kg DCP Type | No. | 70
4.4.3 | Fire extinguishers - 5kg CO2 Type | No. | 30
4.4.4 | Fire extinguishers - 2,5kg CO2 Type | No. | 30
Carried to final summary 4 |  |  |  |  | 0

## CORRECTIVE MAINTENANCE YR 2
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
CALL OUT RATES
BILL 4a - YEAR 2
All rates to be VAT Exclusive
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
4a | STAFF RATES
4a.1 | Corrective Maintenance
4a.1.1 | Technician (Office Hours) | Hr | 120
4a.1.2 | Technician (After Hours) | Hr | 80
4a.1.3 | Artisan (Office Hours) | Hr | 120
4a.1.4 | Artisan (After Hours) | Hr | 80
4a.2 | Call Outs (Including travelling)
4a.2.1 | Call out - Office Hours | No. | 30
4a.2.2 | Call out - After Hours | No. | 20
4a.3 | Spares Mark Up (for evaluation R1000000)
4a.3.1 | less than R20 000 | sum
4a.3.2 | Contractor's Mark Up | % |  | 20000
4a.3.3 | 20001 to R50000 | sum | - | -
4a.3.4 | Contractor's Mark Up | % |  | 50000
4a.3.5 | more than R50000 | sum
4a.3.6 | Contractor's Mark Up | % | 0 | 830000
4a.4 | Replace Fire Extinguishers
4a.4.1 | Fire extinguishers - 4.5kg DCP Type | No. | 48
4a.4.2 | Fire extinguishers - 9kg DCP Type | No. | 70
4a.4.3 | Fire extinguishers - 5kg CO2 Type | No. | 30
4a.4.4 | Fire extinguishers - 2,5kg CO2 Type | No. | 30
Carried to final summary 4a |  |  |  |  | 0

## CORRECTIVE MAINTENANCE YR 3
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
CALL OUT RATES
BILL 4b - YEAR 3
All rates to be VAT Exclusive
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
4b | STAFF RATES
4b.1 | Corrective Maintenance
4b.1.1 | Technician (Office Hours) | Hr | 120
4b.1.2 | Technician (After Hours) | Hr | 80
4b.1.3 | Artisan (Office Hours) | Hr | 120
4b.1.4 | Artisan (After Hours) | Hr | 80
4b.2 | Call Outs (Including travelling)
4b.2.1 | Call out - Office Hours | No. | 30
4b.2.2 | Call out - After Hours | No. | 20
4b.3 | Spares Mark Up (for evaluation R1000000)
4b.3.1 | less than R20 000 | sum
4b.3.2 | Contractor's Mark Up | % |  | 20000
4b.3.3 | 20001 to R50000 | sum | - | -
4b.3.4 | Contractor's Mark Up | % |  | 50000
4b.3.5 | more than R50000 | sum
4b.3.6 | Contractor's Mark Up | % | 0 | 830000
4b.4 | Replace Fire Extinguishers
4b.4.1 | Fire extinguishers - 4.5kg DCP Type | No. | 48
4b.4.2 | Fire extinguishers - 9kg DCP Type | No. | 70
4b.4.3 | Fire extinguishers - 5kg CO2 Type | No. | 30
4b.4.4 | Fire extinguishers - 2,5kg CO2 Type | No. | 30
Carried to final summary 4b |  |  |  |  | 0

## CORRECTIVE MAINTENANCE YR 4
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
CALL OUT RATES
BILL 4c - YEAR 4
All rates to be VAT Exclusive
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
4c | STAFF RATES
4c.1 | Corrective Maintenance
4c.1.1 | Technician (Office Hours) | Hr | 120
4c.1.2 | Technician (After Hours) | Hr | 80
4c.1.3 | Artisan (Office Hours) | Hr | 120
4c.1.4 | Artisan (After Hours) | Hr | 80
4c.2 | Call Outs (Including travelling)
4c.2.1 | Call out - Office Hours | No. | 30
4c.2.2 | Call out - After Hours | No. | 20
4c.3 | Spares Mark Up (for evaluation R1000000)
4c.3.1 | less than R20 000 | sum
4c.3.2 | Contractor's Mark Up | % |  | 20000
4c.3.3 | 20001 to R50000 | sum | - | -
4c.3.4 | Contractor's Mark Up | % |  | 50000
4c.3.5 | more than R50000 | sum
4c.3.6 | Contractor's Mark Up | % | 0 | 830000
4c.4 | Replace Fire Extinguishers
4c.4.1 | Fire extinguishers - 4.5kg DCP Type | No. | 48
4c.4.2 | Fire extinguishers - 9kg DCP Type | No. | 70
4c.4.3 | Fire extinguishers - 5kg CO2 Type | No. | 30
4c.4.4 | Fire extinguishers - 2,5kg CO2 Type | No. | 30
Carried to final summary 4c |  |  |  |  | 0

## CORRECTIVE MAINTENANCE YR 5
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
CALL OUT RATES
BILL 4d - YEAR 5
All rates to be VAT Exclusive
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
4d | STAFF RATES
4d.1 | Corrective Maintenance
4d.1.1 | Technician (Office Hours) | Hr | 120
4d.1.2 | Technician (After Hours) | Hr | 80
4d.1.3 | Artisan (Office Hours) | Hr | 120
4d.1.4 | Artisan (After Hours) | Hr | 80
4d.2 | Call Outs (Including travelling)
4d.2.1 | Call out - Office Hours | No. | 30
4d.2.2 | Call out - After Hours | No. | 20
4d.3 | Spares Mark Up (for evaluation R1000000)
4d.3.1 | less than R20 000 | sum
4d.3.2 | Contractor's Mark Up | % |  | 20000
4d.3.3 | 20001 to R50000 | sum | - | -
4d.3.4 | Contractor's Mark Up | % |  | 50000
4d.3.5 | more than R50000 | sum
4d.3.6 | Contractor's Mark Up | % | 0 | 830000
4d.4 | Replace Fire Extinguishers
4d.4.1 | Fire extinguishers - 4.5kg DCP Type | No. | 48
4d.4.2 | Fire extinguishers - 9kg DCP Type | No. | 70
4d.4.3 | Fire extinguishers - 5kg CO2 Type | No. | 30
4d.4.4 | Fire extinguishers - 2,5kg CO2 Type | No. | 30
Carried to final summary 4d |  |  |  |  | 0

## PRESSURE TESTING
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY WEST CAMPUS
All rates to be VAT Exclusive
BILL 5
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
FIRE FIGHTING EQUIPMENT
5 | WEST CAMPUS
5.1 | Hydrostatic testing of cylinders
5,6,7 | Hydrostatic testing of cylinders – hydrostatic testing to be conducted after every 5 years - 4.5kg DCP | No. | 1131.9
5,6,8 | Hydrostatic testing of cylinders – hydrostatic testing to be conducted after every 5 years - 9.0kg DCP | No. | 1623.6
5,6,9 | Hydrostatic testing of cylinders – hydrostatic testing to be conducted after every 10 year - 5kg CO2 | No. | 627
5,6,10 | Hydrostatic testing of cylinders – hydrostatic testing to be conducted after every 10 years - 2,5kg CO2 | No. | 361.9
5.2 | Fire pumps
5,2,1 | Pressure test pump casing - every 5 years | No. | 2
5,2,2 | Inspect impeller and wear rings - every 5 years | No. | 2
5,2,3 | Overhaul Sprinkler Valve | No. | 9
Carried to final summary 5

## FINAL
SCHEDULE OF QUANTITIES: SERVICING AND REPAIR WORK OF FIRE FIGHTING EQUIPMENT
WITS UNIVERSITY - WEST CAMPUS - FINAL COLLECTION PAGE
ITEM | DESCRIPTION | UNIT | QUANTITY | AMOUNT
1 | BILL 1:Health and Safety Compliance ( safety files) | Sum | 1
2 | BILL 2: INSPECTION | Sum | 1
3 | BILL 3: YEARLY SERVICE | Sum | 1
The bidder is to allow for subsequent escalations for subsequent years. The indicated amount shall be the total from the previous year PLUS the escalation amount. The indicated escalation percentage shall be applied as indicated for each amount when claiming.
3a | Escalated total for item 3 above. Applicable for year 2 (fixed percentage for the duration of the contract) | Percentage | __________%
3b | Escalated total for item 3a above. Applicable for year 3(fixed percentage for the duration of the contract) | Percentage | __________%
3c | Escalated total for item 3b above. Applicable for year 4 (fixed percentage for the duration of the contract) | Percentage | __________%
3d | Escalated total for item 3c above. Applicable for year 5(fixed percentage for the duration of the contract) | Percentage | __________%
4 | CORRECTIVE MAINATENANCE YEAR 1 | Sum | 1
4a | Corrective Maintenance (Year 2) | Sum | 1
4b | Corrective Maintenance (Year 3) | Sum | 1
4c | Corrective Maintenance (Year 4) | Sum | 1
4d | Corrective Maintenance (Year 5) | Sum | 1
5 | BILL 5: PRESSURE TESTING | Sum | 1
TOTAL EXCLUDING VAT |  |  |  | 0
ADD 15% VAT |  |  |  | 0
TOTAL INCLUDING VAT |  |  |  | 0