## Summary Page
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | SUMMARY
Rev: | 1
ITEM | DESCRIPTION | AMOUNT
SUMMARY
1 | PRELIMINARIES AND GENERAL AS PER THE CONDITIONS OF THE CONTRACT
2 | DX IN-ROW COOLERS - SCHEME A (Vertiv Liebert CRV / CRD or equal approved) | 458546.734
3 | DX IN-ROW COOLERS - 42kW UPGRADE OPTION (SCHEME A) (Vertiv Liebert CRV / CRD or equal approved) | 458546.734
| DX IN-ROW COOLERS - SCHEME B (Schneider Electric Uniflair / STULZ CyberRow or equal approved) | 458546.734
| DX IN-ROW COOLERS - 42kW UPGRADE OPTION (SCHEME B) (Schneider Electric Uniflair / STULZ CyberRow or equal approved) | 458546.734
5 | DX SPLIT - UPS 7.1 kW | 30000
Note: The Contractor is to complete the Technical Data Sheet attached to this BOQ for all the schemes
| Total Summary Excl VAT | 1864186.936
| VAT @ 15% | 279628.0404
| Total Summary Incl VAT | 2143814.9764
| Total (Carried forward to Master Summary Page) | 2143814.9764

## Preliminaries and General Items
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | PRELIMINARIES AND GENERAL AS PER THE CONDITIONS OF THE CONTRACT
Rev: | 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PRELIMINARIES AND GENERAL AS PER THE CONDITIONS OF THE CONTRACT
The Framework Schedule of rates is applicable to all Model Projects and Package Orders.
FIXED PRELIMINARIES
Health and safety
1 | Plan, file and basic Mandatories (refer to Annexure 5) | Item | 1
Non-standard rigging on the Client's property
2 | Mobile crane as per the Tender briefing document, Annexure 2 (crane specification to be submitted with tender) | day | 1
Non-standard scaffolding
Note: Scaffolding for builderswork excluded and to be priced during construction
3 | Scaffolding (if required for the Model project) | Item | 1
Maintenance and guarantee
4 | One year's maintenance and guarantee | Item | 1
Additional Fixed Preliminaries items
5 | Items which are not covered in the items above or in the Bill of Quantities and falls within the Preliminaries and General definition as per the Scope, Annexure 2 (list to be provided with the tender) | Item | 1
MONTHLY PRELIMINARIES
Health and safety compliance including Part-time Health and Safety Officer (cost per month)
Note: Tenderers to only price applicable item for the Model project.
6 | Cost per month where Total of the Prices is R 0 to R 2 million ONLY WHEN high-risk factors are applicable | Mnth | 3
7 | Cost per month where Total of the Prices is R 2 million to R 5 million | Mnth | 3
8 | Cost per month where Total of the Prices is R 5 million to R 20 million | Mnth | 3
Additional Monthly Preliminaries items
9 | Items which are not covered in the items above or in the Bill of Quantities and falls within the Preliminaries and General definition as per the Scope, Annexure 2 (list to be provided with the tender) | Item | 1
EQUIPMENT
Site enclosure, hoarding, temporary screens, etc.
10 | 1.80m High galvanised diamond mesh fence tied to and including galvanised posts, stays, etc. fixed in ground and covered with 50% green shade cloth | m | 40
11 | 900 x 1 800mm High single gate to suit fencing and covered with galvanised wire mesh and 50% shade cloth, including hinges, heavy duty lockable barrel bolt and 51mm "Union 3122" padlock | No | 1
12 | 6 000 x 1 800mm High double leaf gate covered with galvanised wire mesh and 50% shade cloth, including hinges, heavy duty lockable barrel bolt and 51mm "Union 3122" padlock | No |  |  | Rate only
13 | Drywall barricade 2.7m high of galvanised steel channel section rails and studs covered on one side with 12,5mm gypsum plasterboard and finished with two coats interior quality PVA emulsion paint, including corners, ends, etc. | m | 20
14 | Extra over preceding item for hollow core single door 813 x 2032mm high, including steel frame, two-lever mortice lock, primer and two coats paint | No | 1
Additional Equipment Preliminaries items
15 | Items which are not covered in the items above or in the Bill of Quantities and falls within the Preliminaries and General definition as per the Scope, Annexure 2 (list to be provided with the tender) | Item | 1

## DX In-Row 29kW - Scheme A
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX IN-ROW COOLERS 29kW - SCHEME A
Rev: | 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX IN-ROW COOLERS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion (DX) in-row cooling units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package, as a like-for-like replacement of the existing in-row cooling units. Scope comprises five (5) COOLING-ONLY in-row units and one (1) FULL-FUNCTION in-row unit (integral humidifier, electric reheat and active dehumidification) for room humidity control. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the Contractor for site conditions (approx. 1 750 m a.s.l., Johannesburg; ambient per Specification). INDOOR UNITS per Specification including unit-mounted controllers c/w wiring, filters and filter frames, condensate drain provision, connection to electrical isolator within 1 m (provided adjacent, by others) and all required accessories. OUTDOOR UNITS per Specification including galvanised/anti-corrosion mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR IN-ROW UNITS - COOLING-ONLY (Supply & Install)
2.1.1 | In-row cooling-only units - CLM-IRC-01 to CLM-IRC-05 (5 No.). Total cooling capacity 30.3 kW, sensible 29 kW per unit (derated for site altitude). Vertiv Liebert CRV / CRD or equal approved. Complete with EC fans, electronic expansion valve (EEV) as per TDS. Confirm unit model against TDS before tender issue. | no | 5 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - selected for unit operating weight | no | 5 |  | 0
2.1.3 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover | set | 10 |  | 0
2.1.4 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 5 |  | 0
2.1.5 | S-trap condensate drain connection - fabricated and fitted | no | 5 |  | 0
2.1.6 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 5 |  | 0
2.1.7 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 5 |  | 0
2.1.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor In-Row Units |  |  | Subtotal | 0
2.2 | INDOOR IN-ROW UNIT - FULL-FUNCTION (Supply & Install)
2.2.1 | Full-function in-row unit - CLM-IRC-06 (1 No.). Total cooling 30.3 kW, sensible 29 kW (derated). Vertiv Liebert CRV / CRD or equal approved, full-function variant providing temperature AND humidity control for the data hall. Complete with EC fans, EEV as per TDS. | no | 1 |  | 0
2.2.2 | Integral humidifier - 3.0 kg/h | no | 1 |  | 0
2.2.3 | Electric reheat element(s) - 7.5 kW | no | 1 |  | 0
2.2.4 | Anti-vibration mounts (AVM) / TICO pads | no | 1 |  | 0
2.2.5 | Filter sets - one for commissioning plus one at handover (total 2 sets) | set | 2 |  | 0
2.2.6 | Refrigerant leak detection sensor | no | 1 |  | 0
2.2.7 | S-trap condensate drain connection PLUS humidifier drain connection | no | 1 |  | 0
2.2.8 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 1 |  | 0
2.2.9 | Equipment labelling - engraved Traffolyte, asset tags, schematic identification | no | 1 |  | 0
2.2.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Indoor In-Row Unit |  |  | Subtotal | 0
2.3 | OUTDOOR CONDENSER UNITS - Supply & Install
2.3.1 | Air-cooled condenser units - CLM-IRC-CND-01 to 06 (6 No.), matched to indoor units, c/w flooded receiver , EC condenser fans, IP54 minimum, derated for site altitude/ambient | no | 6 |  | 0
2.3.2 | Steel frame for condensing units c/w TICO pads / vibration isolators (400mm Height) | no | 6 |  | 0
2.3.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 6 |  | 0
2.3.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 6 |  | 0
2.3.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Outdoor Condenser Units |  |  | Subtotal | 0
2.4 | REFRIGERANT PIPING SYSTEM
2.4.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), refrigeration-grade copper, including bends, joints and brazed connections | m | 240 |  | 0
2.4.2 | Cable trays piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer (existing refrigerant pipe trays / supports to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.4.3 | Filter drier (one per circuit) | no | 6 |  | 0
2.4.4 | Sight glass with moisture indicator (one per circuit) | no | 6 |  | 0
2.4.5 | Insulation for new refrigerant piping | m | 240 |  | 0
2.4.6 | Pipe identification labels and flow-direction arrows | set | 6 |  | 0
2.4.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Refrigerant Piping System |  |  | Subtotal | 0
2.5 | CONDENSATE & HUMIDIFIER WATER / DRAINAGE
2.5.1 | Condensate drain piping c/w S-trap, to full-bore drain point | m | 60 |  | 0
2.5.2 | Condensate pump | no | 6 |  | 0
2.5.3 | Overflow alarm wired back to unit controls | no | 6 |  | 0
2.5.4 | Insulation on condensate pipework (anti-sweat) | m | 60 |  | 0
2.5.5 | Humidifier make-up water supply - connection, isolation valve and strainer (full-function unit) | no | 1 |  | 0
2.5.6 | Humidifier drain connection to waste / tundish (full-function unit) | no | 1 |  | 0
2.5.7 | Piping incluing supports, brackets and clips for humidifier | m | 60 |  | 0
2.5.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Condensate & Humidifier Water / Drainage |  |  | Subtotal | 0
2.6 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX in-row units and fans, including DBs, local starter / isolator, controls etc. In accordance with the Specification attached to the tender package. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories. Note the full-function unit carries an additional electrical load for its humidifier and electric reheat - size the dedicated circuit accordingly.
2.6.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit terminals) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 30 |  | 0
2.6.2 | Electrical cable reticulation - Outdoor Unit (from unit to condenser) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.6.3 | Cable trays / wireways / containment between units (galvanised) - existing trays to be inspected and reused where in good condition, otherwise replaced | m | 240 |  | 0
2.6.4 | Cable glands, lugs and terminations | sum | 1 |  | 0
2.6.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Electrical Installation |  |  | Subtotal | 0
2.7 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.7.1 | BACnet IP interface card per unit | no | 6 |  | 0
2.7.2 | Unit-to-unit interlink cabling for group / teamwork supervisory operation (per manufacturer) | no | 6 |  | 0
2.7.3 | Remote temperature (cold-aisle / supply / return) | no | 12 |  | 0
2.7.4 | RH sensors (return air / cold aisle / supply) | no | 12
2.7.5 | Humidity control configuration - full-function unit set as lead humidity controller; cooling-only units sensible-only. Configure to avoid demand-fighting. | Sum | 1 |  | 0
2.7.6 | Temperature sensors for fan-speed control | no | 6 |  | 0
2.7.7 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.7.8 | BACnet points list verification & integration with existing site BMS head-end | Sum | 1 |  | 0
2.7.9 | BMS graphics development and integration on existing head-end (6 units) | Sum | 1 |  | 0
2.7.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - Controls, Instrumentation & Bms Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Concrete plinths / housekeeping pads for outdoor condensers (reinforced) | sum | 1 |  | Included in the provisional sum below
2.8.2 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate) | sum | 1
2.8.3 | Additional item necessary for completion - contractor to describe
2.8.4 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work & Civils (Provisional sum) |  |  | Subtotal | 458546.734
2.9 | HOT / COLD AISLE CONTAINMENT - DISASSEMBLY & REASSEMBLY
The new in-row units are installed into existing hot/cold-aisle containment. The Contractor shall open (disassemble) the existing containment locally at each in-row position to permit removal of the redundant units and installation of the new units, then reinstate (reassemble) and re-seal the containment to restore airflow integrity. All work in a live data hall - maintain separation, dust control and airflow management throughout.
2.9.1 | Disassembly of existing hot/cold-aisle containment panels / doors locally at each in-row position to allow removal & installation | sum | 1 |  | 0
2.9.2 | Temporary blanking / airflow management during works in the live hall | Sum | 1 |  | 0
2.9.3 | Reassembly & re-sealing of containment after install; restore airflow integrity | sum | 1 |  | 0
2.9.4 | Replacement of any damaged containment panels / seals / brush grommets | Sum | 1 |  | 0
2.9.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Hot / Cold Aisle Containment |  |  | Subtotal | 0
2.10 | TESTING & COMMISSIONING
2.10.1 | Refrigerant pressure test certificate per circuit (nitrogen) | no | 6 |  | 0
2.10.2 | Performance testing - measured capacity, EER, SFP | no | 6 |  | 0
2.10.3 | Air balance testing - supply / return airflows, velocity over coil | no | 6 |  | 0
2.10.4 | Humidity control functional test (full-function unit) - humidify / dehumidify / reheat | no | 1 |  | 0
2.10.5 | Noise level testing - Lp @ 2 m measurement | no | 6 |  | 0
2.10.6 | Functional / integrated systems testing | no | 6 |  | 0
2.10.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.10.8 | Vacuum / dehydration to <500 microns including standing test | no | 6 |  | 0
2.10.9 | Controls commissioning, sensor calibration, alarm verification, setpoint handover | sum | 1
2.10.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.10.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Testing & Commissioning |  |  | Subtotal | 0
2.11 | SPARES & RECOMMENDED CONSUMABLES
2.11.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.11.2 | Supplier to submit list
2.11.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.11 - Spares & Recommended Consumables |  |  | Subtotal | 0
2.12 | DECOMMISSIONING & REMOVAL OF EXISTING IN-ROW UNITS
Decommissioning and removal of the existing six (6) in-row cooling units and their associated condensers. Isolate, recover refrigerant (with disposal certificate), drain, disconnect, remove from site and dispose at an authorised facility.
2.12.1 | Decommission existing in-row indoor units (isolate, drain, disconnect) | no | 6 |  | 0
2.12.2 | Decommission existing condenser units (isolate, disconnect) | no | 6 |  | 0
2.12.3 | Refrigerant recovery, reclaim and disposal certificate | no | 6 |  | 0
2.12.4 | Removal of existing equipment from site, transport and authorised disposal (indoor + outdoor) | set | 6 |  | 0
2.12.5 | Removal of existing pipes and cables | Sum | 1 |  | 0
2.12.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.12.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.12 - Decommissioning & Removal Of Existing In-Row Units |  |  | Subtotal | 0
2.13 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation. NOTE: additional items may NOT be claimed at a later stage unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities.
2.13.1 |  |  |  |  | 0
2.13.2 |  |  |  |  | 0
2.13.3 |  |  |  |  | 0
2.13.4 |  |  |  |  | 0
2.13.5 |  |  |  |  | 0
2.13.6 |  |  |  |  | 0
| Subtotal 2.13 - Additional Items |  |  | Subtotal | 0
| BILL - DX IN-ROW COOLERS (SCHEME A) |  |  | SUB-TOTAL | 458546.734
Carried forward to Summary Page →

## DX In-Row 29kW - Scheme B
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX IN-ROW COOLERS 29kW - SCHEME B
Rev: | 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX IN-ROW COOLERS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion (DX) in-row cooling units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package, as a like-for-like replacement of the existing in-row cooling units. Scope comprises five (5) COOLING-ONLY in-row units and one (1) FULL-FUNCTION in-row unit (integral humidifier, electric reheat and active dehumidification) for room humidity control. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the Contractor for site conditions (approx. 1 750 m a.s.l., Johannesburg; ambient per Specification). INDOOR UNITS per Specification including unit-mounted controllers c/w wiring, filters and filter frames, condensate drain provision, connection to electrical isolator within 1 m (provided adjacent, by others) and all required accessories. OUTDOOR UNITS per Specification including galvanised/anti-corrosion mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR IN-ROW UNITS - COOLING-ONLY (Supply & Install)
2.1.1 | In-row cooling-only units - CLM-IRC-01 to CLM-IRC-05 (5 No.). Total cooling capacity 30.3 kW, sensible 29 kW per unit (derated for site altitude). Schneider Electric Uniflair / STULZ CyberRow or equal approved. Complete with EC fans, electronic expansion valve (EEV) as per TDS. Confirm unit model against TDS before tender issue. | no | 5 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - selected for unit operating weight | no | 5 |  | 0
2.1.3 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover | set | 10 |  | 0
2.1.4 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 5 |  | 0
2.1.5 | S-trap condensate drain connection - fabricated and fitted | no | 5 |  | 0
2.1.6 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 5 |  | 0
2.1.7 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 5 |  | 0
2.1.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor In-Row Units |  |  | Subtotal | 0
2.2 | INDOOR IN-ROW UNIT - FULL-FUNCTION (Supply & Install)
2.2.1 | Full-function in-row unit - CLM-IRC-06 (1 No.). Total cooling 30.3 kW, sensible 29 kW (derated). Schneider Electric Uniflair / STULZ CyberRow or equal approved, full-function variant providing temperature AND humidity control for the data hall. Complete with EC fans, EEV as per TDS. | no | 1 |  | 0
2.2.2 | Integral humidifier - 3.0 kg/h | no | 1 |  | 0
2.2.3 | Electric reheat element(s) - 7.5 kW | no | 1 |  | 0
2.2.4 | Anti-vibration mounts (AVM) / TICO pads | no | 1 |  | 0
2.2.5 | Filter sets - one for commissioning plus one at handover (total 2 sets) | set | 2 |  | 0
2.2.6 | Refrigerant leak detection sensor | no | 1 |  | 0
2.2.7 | S-trap condensate drain connection PLUS humidifier drain connection | no | 1 |  | 0
2.2.8 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 1 |  | 0
2.2.9 | Equipment labelling - engraved Traffolyte, asset tags, schematic identification | no | 1 |  | 0
2.2.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Indoor In-Row Unit |  |  | Subtotal | 0
2.3 | OUTDOOR CONDENSER UNITS - Supply & Install
2.3.1 | Air-cooled condenser units - CLM-IRC-CND-01 to 06 (6 No.), matched to indoor units, c/w flooded receiver , EC condenser fans, IP54 minimum, derated for site altitude/ambient | no | 6 |  | 0
2.3.2 | Steel frame for condensing units c/w TICO pads / vibration isolators (400mm Height) | no | 6 |  | 0
2.3.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 6 |  | 0
2.3.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 6 |  | 0
2.3.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Outdoor Condenser Units |  |  | Subtotal | 0
2.4 | REFRIGERANT PIPING SYSTEM
2.4.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), refrigeration-grade copper, including bends, joints and brazed connections | m | 240 |  | 0
2.4.2 | Cable trays piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer (existing refrigerant pipe trays / supports to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.4.3 | Filter drier (one per circuit) | no | 6 |  | 0
2.4.4 | Sight glass with moisture indicator (one per circuit) | no | 6 |  | 0
2.4.5 | Insulation for new refrigerant piping | m | 240 |  | 0
2.4.6 | Pipe identification labels and flow-direction arrows | set | 6 |  | 0
2.4.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Refrigerant Piping System |  |  | Subtotal | 0
2.5 | CONDENSATE & HUMIDIFIER WATER / DRAINAGE
2.5.1 | Condensate drain piping c/w S-trap, to full-bore drain point | m | 60 |  | 0
2.5.2 | Condensate pump | no | 6 |  | 0
2.5.3 | Overflow alarm wired back to unit controls | no | 6 |  | 0
2.5.4 | Insulation on condensate pipework (anti-sweat) | m | 60 |  | 0
2.5.5 | Humidifier make-up water supply - connection, isolation valve and strainer (full-function unit) | no | 1 |  | 0
2.5.6 | Humidifier drain connection to waste / tundish (full-function unit) | no | 1 |  | 0
2.5.7 | Piping incluing supports, brackets and clips for humidifier | m | 60 |  | 0
2.5.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Condensate & Humidifier Water / Drainage |  |  | Subtotal | 0
2.6 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX in-row units and fans, including DBs, local starter / isolator, controls etc. In accordance with the Specification attached to the tender package. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories. Note the full-function unit carries an additional electrical load for its humidifier and electric reheat - size the dedicated circuit accordingly.
2.6.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit terminals) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 30 |  | 0
2.6.2 | Electrical cable reticulation - Outdoor Unit (from unit to condenser) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.6.3 | Cable trays / wireways / containment between units (galvanised) - existing trays to be inspected and reused where in good condition, otherwise replaced | m | 240 |  | 0
2.6.4 | Cable glands, lugs and terminations | sum | 1 |  | 0
2.6.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Electrical Installation |  |  | Subtotal | 0
2.7 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.7.1 | BACnet IP interface card per unit | no | 6 |  | 0
2.7.2 | Unit-to-unit interlink cabling for group / teamwork supervisory operation (per manufacturer) | no | 6 |  | 0
2.7.3 | Remote temperature (cold-aisle / supply / return) | no | 12 |  | 0
2.7.4 | RH sensors (return air / cold aisle / supply) | no | 12
2.7.5 | Humidity control configuration - full-function unit set as lead humidity controller; cooling-only units sensible-only. Configure to avoid demand-fighting. | Sum | 1 |  | 0
2.7.6 | Temperature sensors for fan-speed control | no | 6 |  | 0
2.7.7 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.7.8 | BACnet points list verification & integration with existing site BMS head-end | Sum | 1 |  | 0
2.7.9 | BMS graphics development and integration on existing head-end (6 units) | Sum | 1 |  | 0
2.7.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - Controls, Instrumentation & Bms Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Concrete plinths / housekeeping pads for outdoor condensers (reinforced) | sum | 1 |  | Included in the provisional sum below
2.8.2 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate) | sum | 1
2.8.3 | Additional item necessary for completion - contractor to describe
2.8.4 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work & Civils (Provisional sum) |  |  | Subtotal | 458546.734
2.9 | HOT / COLD AISLE CONTAINMENT - DISASSEMBLY & REASSEMBLY
The new in-row units are installed into existing hot/cold-aisle containment. The Contractor shall open (disassemble) the existing containment locally at each in-row position to permit removal of the redundant units and installation of the new units, then reinstate (reassemble) and re-seal the containment to restore airflow integrity. All work in a live data hall - maintain separation, dust control and airflow management throughout.
2.9.1 | Disassembly of existing hot/cold-aisle containment panels / doors locally at each in-row position to allow removal & installation | sum | 1 |  | 0
2.9.2 | Temporary blanking / airflow management during works in the live hall | Sum | 1 |  | 0
2.9.3 | Reassembly & re-sealing of containment after install; restore airflow integrity | sum | 1 |  | 0
2.9.4 | Replacement of any damaged containment panels / seals / brush grommets | Sum | 1 |  | 0
2.9.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Hot / Cold Aisle Containment |  |  | Subtotal | 0
2.10 | TESTING & COMMISSIONING
2.10.1 | Refrigerant pressure test certificate per circuit (nitrogen) | no | 6 |  | 0
2.10.2 | Performance testing - measured capacity, EER, SFP | no | 6 |  | 0
2.10.3 | Air balance testing - supply / return airflows, velocity over coil | no | 6 |  | 0
2.10.4 | Humidity control functional test (full-function unit) - humidify / dehumidify / reheat | no | 1 |  | 0
2.10.5 | Noise level testing - Lp @ 2 m measurement | no | 6 |  | 0
2.10.6 | Functional / integrated systems testing | no | 6 |  | 0
2.10.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.10.8 | Vacuum / dehydration to <500 microns including standing test | no | 6 |  | 0
2.10.9 | Controls commissioning, sensor calibration, alarm verification, setpoint handover | sum | 1
2.10.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.10.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Testing & Commissioning |  |  | Subtotal | 0
2.11 | SPARES & RECOMMENDED CONSUMABLES
2.11.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.11.2 | Supplier to submit list
2.11.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.11 - Spares & Recommended Consumables |  |  | Subtotal | 0
2.12 | DECOMMISSIONING & REMOVAL OF EXISTING IN-ROW UNITS
Decommissioning and removal of the existing six (6) in-row cooling units and their associated condensers. Isolate, recover refrigerant (with disposal certificate), drain, disconnect, remove from site and dispose at an authorised facility.
2.12.1 | Decommission existing in-row indoor units (isolate, drain, disconnect) | no | 6 |  | 0
2.12.2 | Decommission existing condenser units (isolate, disconnect) | no | 6 |  | 0
2.12.3 | Refrigerant recovery, reclaim and disposal certificate | no | 6 |  | 0
2.12.4 | Removal of existing equipment from site, transport and authorised disposal (indoor + outdoor) | set | 6 |  | 0
2.12.5 | Removal of existing pipes and cables | Sum | 1 |  | 0
2.12.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.12.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.12 - Decommissioning & Removal Of Existing In-Row Units |  |  | Subtotal | 0
2.13 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation. NOTE: additional items may NOT be claimed at a later stage unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities.
2.13.1 |  |  |  |  | 0
2.13.2 |  |  |  |  | 0
2.13.3 |  |  |  |  | 0
2.13.4 |  |  |  |  | 0
2.13.5 |  |  |  |  | 0
2.13.6 |  |  |  |  | 0
| Subtotal 2.13 - Additional Items |  |  | Subtotal | 0
| BILL - DX IN-ROW COOLERS (OPTIONAL SCHEME B) |  |  | SUB-TOTAL | 458546.734
Carried forward to Summary Page →

## DX In-Row 42kW - Scheme A
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX IN-ROW COOLERS 42kW - SCHEME A
Rev: | 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX IN-ROW COOLERS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion (DX) in-row cooling units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package, as a like-for-like replacement of the existing in-row cooling units. Scope comprises five (5) COOLING-ONLY in-row units and one (1) FULL-FUNCTION in-row unit (integral humidifier, electric reheat and active dehumidification) for room humidity control. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the Contractor for site conditions (approx. 1 750 m a.s.l., Johannesburg; ambient per Specification). INDOOR UNITS per Specification including unit-mounted controllers c/w wiring, filters and filter frames, condensate drain provision, connection to electrical isolator within 1 m (provided adjacent, by others) and all required accessories. OUTDOOR UNITS per Specification including galvanised/anti-corrosion mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR IN-ROW UNITS - COOLING-ONLY (Supply & Install)
2.1.1 | In-row cooling-only units - CLM-IRC-01 to CLM-IRC-05 (5 No.). Total cooling capacity 41.7 kW, sensible 39.7 kW per unit (derated for site altitude). Vertiv Liebert CRV / CRD or equal approved. Complete with EC fans, electronic expansion valve (EEV) as per TDS. Confirm unit model against TDS before tender issue. | no | 5 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - selected for unit operating weight | no | 5 |  | 0
2.1.3 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover | set | 10 |  | 0
2.1.4 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 5 |  | 0
2.1.5 | S-trap condensate drain connection - fabricated and fitted | no | 5 |  | 0
2.1.6 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 5 |  | 0
2.1.7 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 5 |  | 0
2.1.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor In-Row Units |  |  | Subtotal | 0
2.2 | INDOOR IN-ROW UNIT - FULL-FUNCTION (Supply & Install)
2.2.1 | Full-function in-row unit - CLM-IRC-06 (1 No.). Total cooling 41.7 kW, sensible 39.7 kW (derated). Vertiv Liebert CRV / CRD or equal approved, full-function variant providing temperature AND humidity control for the data hall. Complete with EC fans, EEV as per TDS. | no | 1 |  | 0
2.2.2 | Integral humidifier - 3.0 kg/h | no | 1 |  | 0
2.2.3 | Electric reheat element(s) - 15 kW | no | 1 |  | 0
2.2.4 | Anti-vibration mounts (AVM) / TICO pads | no | 1 |  | 0
2.2.5 | Filter sets - one for commissioning plus one at handover (total 2 sets) | set | 2 |  | 0
2.2.6 | Refrigerant leak detection sensor | no | 1 |  | 0
2.2.7 | S-trap condensate drain connection PLUS humidifier drain connection | no | 1 |  | 0
2.2.8 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 1 |  | 0
2.2.9 | Equipment labelling - engraved Traffolyte, asset tags, schematic identification | no | 1 |  | 0
2.2.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Indoor In-Row Unit |  |  | Subtotal | 0
2.3 | OUTDOOR CONDENSER UNITS - Supply & Install
2.3.1 | Air-cooled condenser units - CLM-IRC-CND-01 to 06 (6 No.), matched to indoor units, c/w flooded receiver , EC condenser fans, IP54 minimum, derated for site altitude/ambient | no | 6 |  | 0
2.3.2 | Steel frame for condensing units c/w TICO pads / vibration isolators (400mm Height) | no | 6 |  | 0
2.3.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 6 |  | 0
2.3.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 6 |  | 0
2.3.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Outdoor Condenser Units |  |  | Subtotal | 0
2.4 | REFRIGERANT PIPING SYSTEM
2.4.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), refrigeration-grade copper, including bends, joints and brazed connections | m | 240 |  | 0
2.4.2 | Cable trays piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer (existing refrigerant pipe trays / supports to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.4.3 | Filter drier (one per circuit) | no | 6 |  | 0
2.4.4 | Sight glass with moisture indicator (one per circuit) | no | 6 |  | 0
2.4.5 | Insulation for new refrigerant piping | m | 240 |  | 0
2.4.6 | Pipe identification labels and flow-direction arrows | set | 6 |  | 0
2.4.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Refrigerant Piping System |  |  | Subtotal | 0
2.5 | CONDENSATE & HUMIDIFIER WATER / DRAINAGE
2.5.1 | Condensate drain piping c/w S-trap, to full-bore drain point | m | 60 |  | 0
2.5.2 | Condensate pump | no | 6 |  | 0
2.5.3 | Overflow alarm wired back to unit controls | no | 6 |  | 0
2.5.4 | Insulation on condensate pipework (anti-sweat) | m | 60 |  | 0
2.5.5 | Humidifier make-up water supply - connection, isolation valve and strainer (full-function unit) | no | 1 |  | 0
2.5.6 | Humidifier drain connection to waste / tundish (full-function unit) | no | 1 |  | 0
2.5.7 | Piping incluing supports, brackets and clips for humidifier | m | 60 |  | 0
2.5.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Condensate & Humidifier Water / Drainage |  |  | Subtotal | 0
2.6 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX in-row units and fans, including DBs, local starter / isolator, controls etc. In accordance with the Specification attached to the tender package. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories. Note the full-function unit carries an additional electrical load for its humidifier and electric reheat - size the dedicated circuit accordingly.
2.6.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit terminals) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 30 |  | 0
2.6.2 | Electrical cable reticulation - Outdoor Unit (from unit to condenser) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.6.3 | Cable trays / wireways / containment between units (galvanised) - existing trays to be inspected and reused where in good condition, otherwise replaced | m | 240 |  | 0
2.6.4 | Cable glands, lugs and terminations | sum | 1 |  | 0
2.6.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Electrical Installation |  |  | Subtotal | 0
2.7 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.7.1 | BACnet IP interface card per unit | no | 6 |  | 0
2.7.2 | Unit-to-unit interlink cabling for group / teamwork supervisory operation (per manufacturer) | no | 6 |  | 0
2.7.3 | Remote temperature (cold-aisle / supply / return) | no | 12 |  | 0
2.7.4 | RH sensors (return air / cold aisle / supply) | no | 12
2.7.5 | Humidity control configuration - full-function unit set as lead humidity controller; cooling-only units sensible-only. Configure to avoid demand-fighting. | Sum | 1 |  | 0
2.7.6 | Temperature sensors for fan-speed control | no | 6 |  | 0
2.7.7 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.7.8 | BACnet points list verification & integration with existing site BMS head-end | Sum | 1 |  | 0
2.7.9 | BMS graphics development and integration on existing head-end (6 units) | Sum | 1 |  | 0
2.7.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - Controls, Instrumentation & Bms Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Concrete plinths / housekeeping pads for outdoor condensers (reinforced) | sum | 1 |  | Included in the provisional sum below
2.8.2 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate) | sum | 1
2.8.3 | Additional item necessary for completion - contractor to describe
2.8.4 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work & Civils (Provisional sum) |  |  | Subtotal | 458546.734
2.9 | HOT / COLD AISLE CONTAINMENT - DISASSEMBLY & REASSEMBLY
The new in-row units are installed into existing hot/cold-aisle containment. The Contractor shall open (disassemble) the existing containment locally at each in-row position to permit removal of the redundant units and installation of the new units, then reinstate (reassemble) and re-seal the containment to restore airflow integrity. All work in a live data hall - maintain separation, dust control and airflow management throughout.
2.9.1 | Disassembly of existing hot/cold-aisle containment panels / doors locally at each in-row position to allow removal & installation | sum | 1 |  | 0
2.9.2 | Temporary blanking / airflow management during works in the live hall | Sum | 1 |  | 0
2.9.3 | Reassembly & re-sealing of containment after install; restore airflow integrity | sum | 1 |  | 0
2.9.4 | Replacement of any damaged containment panels / seals / brush grommets | Sum | 1 |  | 0
2.9.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Hot / Cold Aisle Containment |  |  | Subtotal | 0
2.10 | TESTING & COMMISSIONING
2.10.1 | Refrigerant pressure test certificate per circuit (nitrogen) | no | 6 |  | 0
2.10.2 | Performance testing - measured capacity, EER, SFP | no | 6 |  | 0
2.10.3 | Air balance testing - supply / return airflows, velocity over coil | no | 6 |  | 0
2.10.4 | Humidity control functional test (full-function unit) - humidify / dehumidify / reheat | no | 1 |  | 0
2.10.5 | Noise level testing - Lp @ 2 m measurement | no | 6 |  | 0
2.10.6 | Functional / integrated systems testing | no | 6 |  | 0
2.10.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.10.8 | Vacuum / dehydration to <500 microns including standing test | no | 6 |  | 0
2.10.9 | Controls commissioning, sensor calibration, alarm verification, setpoint handover | sum | 1
2.10.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.10.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Testing & Commissioning |  |  | Subtotal | 0
2.11 | SPARES & RECOMMENDED CONSUMABLES
2.11.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.11.2 | Supplier to submit list
2.11.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.11 - Spares & Recommended Consumables |  |  | Subtotal | 0
2.12 | DECOMMISSIONING & REMOVAL OF EXISTING IN-ROW UNITS
Decommissioning and removal of the existing six (6) in-row cooling units and their associated condensers. Isolate, recover refrigerant (with disposal certificate), drain, disconnect, remove from site and dispose at an authorised facility.
2.12.1 | Decommission existing in-row indoor units (isolate, drain, disconnect) | no | 6 |  | 0
2.12.2 | Decommission existing condenser units (isolate, disconnect) | no | 6 |  | 0
2.12.3 | Refrigerant recovery, reclaim and disposal certificate | no | 6 |  | 0
2.12.4 | Removal of existing equipment from site, transport and authorised disposal (indoor + outdoor) | set | 6 |  | 0
2.12.5 | Removal of existing pipes and cables | Sum | 1 |  | 0
2.12.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.12.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.12 - Decommissioning & Removal Of Existing In-Row Units |  |  | Subtotal | 0
2.13 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation. NOTE: additional items may NOT be claimed at a later stage unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities.
2.13.1 |  |  |  |  | 0
2.13.2 |  |  |  |  | 0
2.13.3 |  |  |  |  | 0
2.13.4 |  |  |  |  | 0
2.13.5 |  |  |  |  | 0
2.13.6 |  |  |  |  | 0
| Subtotal 2.13 - Additional Items |  |  | Subtotal | 0
| BILL - DX IN-ROW COOLERS (SCHEME A) |  |  | SUB-TOTAL | 458546.734
Carried forward to Summary Page →

## DX In-Row 42kW - Scheme B
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX IN-ROW COOLERS 42kW - SCHEME B
Rev: | 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX IN-ROW COOLERS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion (DX) in-row cooling units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package, as a like-for-like replacement of the existing in-row cooling units. Scope comprises five (5) COOLING-ONLY in-row units and one (1) FULL-FUNCTION in-row unit (integral humidifier, electric reheat and active dehumidification) for room humidity control. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the Contractor for site conditions (approx. 1 750 m a.s.l., Johannesburg; ambient per Specification). INDOOR UNITS per Specification including unit-mounted controllers c/w wiring, filters and filter frames, condensate drain provision, connection to electrical isolator within 1 m (provided adjacent, by others) and all required accessories. OUTDOOR UNITS per Specification including galvanised/anti-corrosion mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR IN-ROW UNITS - COOLING-ONLY (Supply & Install)
2.1.1 | In-row cooling-only units - CLM-IRC-01 to CLM-IRC-05 (5 No.). Total cooling capacity 41.7 kW, sensible 39.7 kW per unit (derated for site altitude). Schneider Electric Uniflair / STULZ CyberRow or equal approved. Complete with EC fans, electronic expansion valve (EEV) as per TDS. Confirm unit model against TDS before tender issue. | no | 5 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - selected for unit operating weight | no | 5 |  | 0
2.1.3 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover | set | 10 |  | 0
2.1.4 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 5 |  | 0
2.1.5 | S-trap condensate drain connection - fabricated and fitted | no | 5 |  | 0
2.1.6 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 5 |  | 0
2.1.7 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 5 |  | 0
2.1.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor In-Row Units |  |  | Subtotal | 0
2.2 | INDOOR IN-ROW UNIT - FULL-FUNCTION (Supply & Install)
2.2.1 | Full-function in-row unit - CLM-IRC-06 (1 No.). Total cooling 41.7 kW, sensible 39.7 kW (derated). Schneider Electric Uniflair / STULZ CyberRow or equal approved, full-function variant providing temperature AND humidity control for the data hall. Complete with EC fans, EEV as per TDS. | no | 1 |  | 0
2.2.2 | Integral humidifier - 3.0 kg/h | no | 1 |  | 0
2.2.3 | Electric reheat element(s) - 15 kW | no | 1 |  | 0
2.2.4 | Anti-vibration mounts (AVM) / TICO pads | no | 1 |  | 0
2.2.5 | Filter sets - one for commissioning plus one at handover (total 2 sets) | set | 2 |  | 0
2.2.6 | Refrigerant leak detection sensor | no | 1 |  | 0
2.2.7 | S-trap condensate drain connection PLUS humidifier drain connection | no | 1 |  | 0
2.2.8 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 1 |  | 0
2.2.9 | Equipment labelling - engraved Traffolyte, asset tags, schematic identification | no | 1 |  | 0
2.2.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Indoor In-Row Unit |  |  | Subtotal | 0
2.3 | OUTDOOR CONDENSER UNITS - Supply & Install
2.3.1 | Air-cooled condenser units - CLM-IRC-CND-01 to 06 (6 No.), matched to indoor units, c/w flooded receiver , EC condenser fans, IP54 minimum, derated for site altitude/ambient | no | 6 |  | 0
2.3.2 | Steel frame for condensing units c/w TICO pads / vibration isolators (400mm Height) | no | 6 |  | 0
2.3.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 6 |  | 0
2.3.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 6 |  | 0
2.3.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Outdoor Condenser Units |  |  | Subtotal | 0
2.4 | REFRIGERANT PIPING SYSTEM
2.4.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), refrigeration-grade copper, including bends, joints and brazed connections | m | 240 |  | 0
2.4.2 | Cable trays piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer (existing refrigerant pipe trays / supports to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.4.3 | Filter drier (one per circuit) | no | 6 |  | 0
2.4.4 | Sight glass with moisture indicator (one per circuit) | no | 6 |  | 0
2.4.5 | Insulation for new refrigerant piping | m | 240 |  | 0
2.4.6 | Pipe identification labels and flow-direction arrows | set | 6 |  | 0
2.4.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Refrigerant Piping System |  |  | Subtotal | 0
2.5 | CONDENSATE & HUMIDIFIER WATER / DRAINAGE
2.5.1 | Condensate drain piping c/w S-trap, to full-bore drain point | m | 60 |  | 0
2.5.2 | Condensate pump | no | 6 |  | 0
2.5.3 | Overflow alarm wired back to unit controls | no | 6 |  | 0
2.5.4 | Insulation on condensate pipework (anti-sweat) | m | 60 |  | 0
2.5.5 | Humidifier make-up water supply - connection, isolation valve and strainer (full-function unit) | no | 1 |  | 0
2.5.6 | Humidifier drain connection to waste / tundish (full-function unit) | no | 1 |  | 0
2.5.7 | Piping incluing supports, brackets and clips for humidifier | m | 60 |  | 0
2.5.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Condensate & Humidifier Water / Drainage |  |  | Subtotal | 0
2.6 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX in-row units and fans, including DBs, local starter / isolator, controls etc. In accordance with the Specification attached to the tender package. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories. Note the full-function unit carries an additional electrical load for its humidifier and electric reheat - size the dedicated circuit accordingly.
2.6.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit terminals) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 30 |  | 0
2.6.2 | Electrical cable reticulation - Outdoor Unit (from unit to condenser) c/w cable tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | m | 240 |  | 0
2.6.3 | Cable trays / wireways / containment between units (galvanised) - existing trays to be inspected and reused where in good condition, otherwise replaced | m | 240 |  | 0
2.6.4 | Cable glands, lugs and terminations | sum | 1 |  | 0
2.6.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Electrical Installation |  |  | Subtotal | 0
2.7 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.7.1 | BACnet IP interface card per unit | no | 6 |  | 0
2.7.2 | Unit-to-unit interlink cabling for group / teamwork supervisory operation (per manufacturer) | no | 6 |  | 0
2.7.3 | Remote temperature (cold-aisle / supply / return) | no | 12 |  | 0
2.7.4 | RH sensors (return air / cold aisle / supply) | no | 12
2.7.5 | Humidity control configuration - full-function unit set as lead humidity controller; cooling-only units sensible-only. Configure to avoid demand-fighting. | Sum | 1 |  | 0
2.7.6 | Temperature sensors for fan-speed control | no | 6 |  | 0
2.7.7 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.7.8 | BACnet points list verification & integration with existing site BMS head-end | Sum | 1 |  | 0
2.7.9 | BMS graphics development and integration on existing head-end (6 units) | Sum | 1 |  | 0
2.7.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - Controls, Instrumentation & Bms Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Concrete plinths / housekeeping pads for outdoor condensers (reinforced) | sum | 1 |  | Included in the provisional sum below
2.8.2 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate) | sum | 1
2.8.3 | Additional item necessary for completion - contractor to describe
2.8.4 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work & Civils (Provisional sum) |  |  | Subtotal | 458546.734
2.9 | HOT / COLD AISLE CONTAINMENT - DISASSEMBLY & REASSEMBLY
The new in-row units are installed into existing hot/cold-aisle containment. The Contractor shall open (disassemble) the existing containment locally at each in-row position to permit removal of the redundant units and installation of the new units, then reinstate (reassemble) and re-seal the containment to restore airflow integrity. All work in a live data hall - maintain separation, dust control and airflow management throughout.
2.9.1 | Disassembly of existing hot/cold-aisle containment panels / doors locally at each in-row position to allow removal & installation | sum | 1 |  | 0
2.9.2 | Temporary blanking / airflow management during works in the live hall | Sum | 1 |  | 0
2.9.3 | Reassembly & re-sealing of containment after install; restore airflow integrity | sum | 1 |  | 0
2.9.4 | Replacement of any damaged containment panels / seals / brush grommets | Sum | 1 |  | 0
2.9.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Hot / Cold Aisle Containment |  |  | Subtotal | 0
2.10 | TESTING & COMMISSIONING
2.10.1 | Refrigerant pressure test certificate per circuit (nitrogen) | no | 6 |  | 0
2.10.2 | Performance testing - measured capacity, EER, SFP | no | 6 |  | 0
2.10.3 | Air balance testing - supply / return airflows, velocity over coil | no | 6 |  | 0
2.10.4 | Humidity control functional test (full-function unit) - humidify / dehumidify / reheat | no | 1 |  | 0
2.10.5 | Noise level testing - Lp @ 2 m measurement | no | 6 |  | 0
2.10.6 | Functional / integrated systems testing | no | 6 |  | 0
2.10.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.10.8 | Vacuum / dehydration to <500 microns including standing test | no | 6 |  | 0
2.10.9 | Controls commissioning, sensor calibration, alarm verification, setpoint handover | sum | 1
2.10.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.10.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Testing & Commissioning |  |  | Subtotal | 0
2.11 | SPARES & RECOMMENDED CONSUMABLES
2.11.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.11.2 | Supplier to submit list
2.11.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.11 - Spares & Recommended Consumables |  |  | Subtotal | 0
2.12 | DECOMMISSIONING & REMOVAL OF EXISTING IN-ROW UNITS
Decommissioning and removal of the existing six (6) in-row cooling units and their associated condensers. Isolate, recover refrigerant (with disposal certificate), drain, disconnect, remove from site and dispose at an authorised facility.
2.12.1 | Decommission existing in-row indoor units (isolate, drain, disconnect) | no | 6 |  | 0
2.12.2 | Decommission existing condenser units (isolate, disconnect) | no | 6 |  | 0
2.12.3 | Refrigerant recovery, reclaim and disposal certificate | no | 6 |  | 0
2.12.4 | Removal of existing equipment from site, transport and authorised disposal (indoor + outdoor) | set | 6 |  | 0
2.12.5 | Removal of existing pipes and cables | Sum | 1 |  | 0
2.12.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.12.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.12 - Decommissioning & Removal Of Existing In-Row Units |  |  | Subtotal | 0
2.13 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation. NOTE: additional items may NOT be claimed at a later stage unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities.
2.13.1 |  |  |  |  | 0
2.13.2 |  |  |  |  | 0
2.13.3 |  |  |  |  | 0
2.13.4 |  |  |  |  | 0
2.13.5 |  |  |  |  | 0
2.13.6 |  |  |  |  | 0
| Subtotal 2.13 - Additional Items |  |  | Subtotal | 0
| BILL - DX IN-ROW COOLERS (OPTIONAL SCHEME B) |  |  | SUB-TOTAL | 458546.734
Carried forward to Summary Page →

## DX Split - UPS Room
Project: | WITS - CLM DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX SPLIT UNITS - UPS ROOM
Rev: | 1
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
3 | DX SPLIT UNITS - UPS ROOM - SUPPLY, INSTALL, TEST & COMMISSION
Supply, install, test and commission four (4) DX split air-conditioning units, 7.1 kW nominal each, serving the UPS room (N+1 arrangement). Including indoor units, matched condensers, refrigerant piping, condensate drainage, electrical connections, controls and volt-free status to the site BMS. All figures derated for site altitude. Refer to TDS and Specification.
3.1 | EQUIPMENT - Supply & Install
3.1.1 | Indoor units - 7.1 kW nominal cooling (high-wall or ceiling cassette), inverter / EC, R410A or R32 for UPS room cooling (N+1) | no | 4 |  | 0
3.1.2 | Matched outdoor condensing units, IP54, derated for altitude/ambient | no | 4 |  | 0
3.1.3 | Wall mounts / brackets / AVM / TICO pads | set | 4 |  | 0
3.1.4 | Wired wall controller / thermostat per unit | no | 4 |  | 0
3.1.5 | Filter sets (one for commissioning + one at handover) | set | 8 |  | 0
3.1.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.1.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.1 - Equipment |  |  | Subtotal | 0
3.2 | REFRIGERANT PIPING
3.2.1 | Refrigerant piping (gas + liquid), copper, incl trunking and insulation | m | 80 |  | 0
3.2.2 | Pipe brackets, supports and hangers (existing refrigerant pipe trays / supports to be inspected and reused where in good condition, otherwise replaced) | m | 80 |  | 0
3.2.3 | Wall / slab penetrations incl sleeves and making good | no | 4 |  | 0
3.2.4 | Refrigerant charge complete with charging | kg | 12 |  | 0
3.2.5 | Nitrogen pressure test per circuit | no | 4 |  | 0
3.2.6 | Vacuum / dehydration to <500 microns | no | 4 |  | 0
3.2.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.2.8 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.2 - Refrigerant Piping |  |  | Subtotal | 0
3.3 | CONDENSATE DRAINAGE
3.3.1 | Condensate drain piping c/w S-trap to drain | m | 30 |  | 0
3.3.2 | Condensate pump where gravity not achievable | no | 4 |  | 0
3.3.3 | Insulation on condensate pipework | m | 30 |  | 0
3.3.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.3.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.3 - Condensate Drainage |  |  | Subtotal | 0
3.4 | ELECTRICAL INSTALLATION
3.4.1 | Cable reticulation - indoor unit (isolator to unit) c/w tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | no | 4 |  | 0
3.4.2 | Cable reticulation - outdoor unit (isolator to condenser) c/w tray (existing cable trays to be inspected and reused where in good condition, otherwise replaced) | no | 4 |  | 0
3.4.3 | Isolators, cable glands, lugs and terminations | sum | 1 |  | 0
3.4.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.4.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.4 - Electrical Installation |  |  | Subtotal | 0
3.5 | CONTROLS & BMS INTEGRATION
3.5.1 | Volt-free run / fault / alarm status to site BMS per unit | no | 4 |  | 0
3.5.2 | BMS integration, points verification and graphics (UPS room) | Sum | 1 |  | 0
3.5.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.5.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.5 - Controls & Bms Integration |  |  | Subtotal | 0
3.6 | BUILDERS WORK
3.6.1 | Core drilling / penetrations for pipe and cable | no | 4 |  | Included in the provisional sum below
3.6.2 | Making good of penetrations and finishes | no | 4
3.6.3 | Brackets and plinths (UPS split units) | Sum | 1
3.6.4 | Additional item necessary for completion - contractor to describe
3.6.5 | Additional item necessary for completion - contractor to describe
| Subtotal 3.6 - Builders Work (Provisional Sum) |  |  | Subtotal | 30000
3.7 | TESTING & COMMISSIONING
3.7.1 | Refrigerant pressure test certificate per circuit | no | 4 |  | 0
3.7.2 | Performance and functional testing (incl N+1 changeover where applicable) | no | 4 |  | 0
3.7.3 | Commissioning report, as-built drawings and O&M manual | Sum | 1 |  | 0
3.7.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.7.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.7 - Testing & Commissioning |  |  | Subtotal | 0
3.8 | DECOMMISSIONING (if applicable)
3.8.1 | Decommission and remove existing UPS-room units where being replaced - recover refrigerant with disposal certificate, remove and dispose (PROVISIONAL) | no | 4 |  | 0
3.8.2 | Additional item necessary for completion - contractor to describe |  |  |  | 0
3.8.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 3.8 - Decommissioning |  |  | Subtotal | 0
3.9 | ADDITIONAL ITEMS BY CONTRACTOR
3.9.1 |  |  |  |  | 0
3.9.2 |  |  |  |  | 0
3.9.3 |  |  |  |  | 0
3.9.4 |  |  |  |  | 0
| Subtotal 3.9 - Additional Items |  |  | Subtotal | 0
| BILL - DX SPLIT UNITS (UPS ROOM) |  |  | SUB-TOTAL | 30000
Carried forward to Summary Page →

## DST - Scheme A
TECHNICAL DATA SHEET - IN-ROW COOLER (Direct Expansion) - SCHEME A (Vertiv Liebert CRV / CRD or equal approved)
PROJECT: WITS - CLM DATA CENTRE ¦ REVISION: 01 ¦ DATE: 19/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all - complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception - confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R - Accept/Reject - Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | CLM-IRC-01 to 06
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 6
8 | Equipment tag numbers | - | See Dwg
9 | Warranty period | Yrs | 1
10 | Unit type | - | In-Row Cooler
11 | Redundancy configuration | - | N+1
1. ENVIRONMENTAL
1 | Site altitude | masl | 1695
2 | Air pressure at altitude (calculated) | kPa | 82.5522
3 | Air density at altitude (calculated) | kg/m³ | 0.96455
4 | Design outdoor dry-bulb temperature (summer) | °C | 37.5
5 | Design outdoor wet-bulb temperature (summer) | °C | 23.6
6 | Design outdoor dry-bulb temperature (winter) | °C | -5.1
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating - indoor unit (IEC 60529) | IP | IP20
9 | IP rating - outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class - dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE - DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 1
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 42
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | ≥0.95 (sensible-only)
12 | Unit inlet air temperature (return from hot aisle) | °C | 32
13 | Off-coil temperature (supply to cold aisle) | °C | 19
14 | Design delta T over unit (calculated) | °C | 13
15 | Unit inlet air relative humidity | % | 30
16 | Cooling efficiency (Total cooling / Total power) - EER | kWth/kW_e | ≥3.0
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT - INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Rear intake / front discharge
3 | Containment type | - | Hot aisle
4 | Airflow (design) - Q/(ρ·Cp·ΔT) | m³/s | 3.3329
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 0
8 | Total pressure drop incl. ESP | Pa | 200
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT - OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS (sensible-only - expect minimal)
Note: In-row units operate primarily on sensible load (no dehumidification) - condensate volumes are minimal. All condensate piping to be installed with minimum fall to prevent standing water.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | In-Row Cooler
2 | Pipework connection (top / side / bottom) | - | Top
3 | Dehumidification cycle | Y/N | No
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | Yes
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications - safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (CBs) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC - indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥6
11 | Temperature control method | - | Supply air temp
12 | Fan speed control method (dP between aisles / dT supply-return) | dP / dT | dP
13 | Supply of differential pressure sensors (installation by others) | Y/N | Yes
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) - min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet - BACnet/IP support | Y/N | Yes
2 | BACnet - BACnet MS/TP support | Y/N | VS
3 | BACnet - PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet - BTL listed | Y/N | VS
5 | BACnet - Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus - Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus - Modbus TCP/IP support | Y/N | VS
8 | Modbus - Register map / points list provided | Y/N | Yes
9 | SNMP - MIB file provided | Y/N | VS
10 | SNMP - Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface - 10/100/1000 Base-T | Y/N | Yes
14. HEATER REQUIREMENT (SENSIBLE-ONLY OPERATION)
In-row coolers operate sensible-only (no dehumidification cycle) - reheat is typically not required. Calculation retained for vendor confirmation if dehumidification is added.
1 | Room / cold aisle temperature setpoint | °C | 24
2 | Minimum acceptable supply air temperature | °C | 18
3 | Design airflow (from Section 4) | m³/s | 3.3329
4 | Air density at altitude (from Section 1) | kg/m³ | 0.96455
5 | Reheat duty required: Q = ρ × V̇ × Cp × (T_room - T_min_supply) | kW | 19.3846
6 | Heater type | - | PTC electric (if fitted)
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | No - sensible-only operation
15. HUMIDIFIER REQUIREMENT
Humidifier sized for worst-case winter infiltration / make-up air. In-row units may share humidification load with a dedicated make-up air unit - adjust infiltration rate per unit accordingly.
1 | Room RH setpoint (minimum) | % | 30
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 5.7
4 | Estimated infiltration / make-up air rate per unit | m³/s | 0.05
5 | Air density (from Section 1) | kg/m³ | 0.96455
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 4.39
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 × 3600 | kg/hr | 0.76219
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.57164
9 | Humidifier type | - | Electrode steam
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable - confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING - INDOOR UNIT
1 | Height | mm | 2000
2 | Width | mm | 600
3 | Depth | mm | 1146
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance - front | mm | VS
7 | Minimum maintenance clearance - rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Top
10 | Rack-compatible footprint (600 mm wide) | Y/N | Yes
11 | Castors / levelling feet supplied | Y/N | Yes
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING - OUTDOOR UNIT
1 | Height | mm | 1245
2 | Width | mm | 1275
3 | Depth | mm | 2365
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Top / Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation - suction line | - | As per manufacturer recommendation
9 | Pipe insulation - liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | No - sensible-only operation
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | No
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Hot aisle containment panel kit (front cover plates) | Y/N | VS
8 | Blanking panels for empty rack-row positions | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | In-row units handle sensible load only - no dehumidification. Latent load to be managed by dedicated make-up air or perimeter equipment.
6 | Hot aisle containment is required for design intent - confirm rack layout and containment panel coordination with civil/structural.
7 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
8 | Humidifier sizing is indicative - vendor to confirm capacity meets or exceeds calculated values for site conditions.
9 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
10 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.
CR

## DST - Full-Function - Scheme A
TECHNICAL DATA SHEET - IN-ROW COOLER (Direct Expansion) - FULL-FUNCTION UNIT - SCHEME A (Vertiv Liebert CRV / CRD or equal approved)
PROJECT: WITS - CLM DATA CENTRE ¦ REVISION: 01 ¦ DATE: 19/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all - complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception - confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R - Accept/Reject - Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | CLM-IRC-06
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 1
8 | Equipment tag numbers | - | CLM-IRC-06
9 | Warranty period | Yrs | 1
10 | Unit type | - | In-Row Cooler - Full-Function (Cooling + Humidity Control)
11 | Redundancy configuration | - | N/A (Standalone unit)
1. ENVIRONMENTAL
1 | Site altitude | masl | 1750
2 | Air pressure at altitude (calculated) | kPa | 81.994
3 | Air density at altitude (calculated) | kg/m³ | 0.95803
4 | Design outdoor dry-bulb temperature (summer) | °C | 37.5
5 | Design outdoor wet-bulb temperature (summer) | °C | 23.6
6 | Design outdoor dry-bulb temperature (winter) | °C | -5.1
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating - indoor unit (IEC 60529) | IP | IP20
9 | IP rating - outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class - dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE - DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 1
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 42
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | 0.75–0.85 (incl. latent load)
12 | Unit inlet air temperature (return from hot aisle) | °C | 38
13 | Off-coil temperature (supply to cold aisle) | °C | 19
14 | Design delta T over unit (calculated) | °C | 19
15 | Unit inlet air relative humidity | % | 30
16 | Cooling efficiency (Total cooling / Total power) - EER | kWth/kW_e | ≥3.0
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT - INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Rear intake / front discharge
3 | Containment type | - | Hot aisle
4 | Airflow (design) - Q/(ρ·Cp·ΔT) | m³/s | 2.2959
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 0
8 | Total pressure drop incl. ESP | Pa | 200
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT - OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS (sensible-only - expect minimal)
Note: In-row units operate primarily on sensible load (no dehumidification) - condensate volumes are minimal. All condensate piping to be installed with minimum fall to prevent standing water.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | In-Row Cooler
2 | Pipework connection (top / side / bottom) | - | Top
3 | Dehumidification cycle | Y/N | Yes
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | Yes
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications - safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (CBs) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC - indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥6
11 | Temperature control method | - | Supply air temp
12 | Fan speed control method (dP between aisles / dT supply-return) | dP / dT | dP
13 | Supply of differential pressure sensors (installation by others) | Y/N | Yes
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) - min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet - BACnet/IP support | Y/N | Yes
2 | BACnet - BACnet MS/TP support | Y/N | VS
3 | BACnet - PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet - BTL listed | Y/N | VS
5 | BACnet - Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus - Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus - Modbus TCP/IP support | Y/N | VS
8 | Modbus - Register map / points list provided | Y/N | Yes
9 | SNMP - MIB file provided | Y/N | VS
10 | SNMP - Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface - 10/100/1000 Base-T | Y/N | Yes
14. ELECTRIC REHEAT REQUIREMENT (DEHUMIDIFICATION)
Full-function unit provides active dehumidification via electric reheat downstream of the cooling coil, working with the compressor sub-cooling / reheat sequence. Vendor to confirm heater capacity meets or exceeds the calculated reheat duty below.
1 | Room / cold aisle temperature setpoint | °C | 38
2 | Minimum acceptable supply air temperature | °C | 18
3 | Design airflow (from Section 4) | m³/s | 2.2959
4 | Air density at altitude (from Section 1) | kg/m³ | 0.95803
5 | Reheat duty required | kW | 7.5
6 | Heater type | - | Electric resistance reheat (SCR/SSR staged control)
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | Yes
15. HUMIDIFIER REQUIREMENT
Humidifier sized for worst-case winter infiltration / make-up air for this dedicated full-function unit, which carries the room's humidification duty (integral electrode-steam humidifier).
1 | Room RH setpoint (minimum) | % | 30
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 5.7
4 | Estimated infiltration / make-up air rate per unit | m³/s | 0.05
5 | Air density (from Section 1) | kg/m³ | 0.95803
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 4.39
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 × 3600 | kg/hr | 0.75703
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.56777
9 | Humidifier type | - | Electrode steam
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable - confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING - INDOOR UNIT
1 | Height | mm | 2000
2 | Width | mm | 600
3 | Depth | mm | 1146
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance - front | mm | VS
7 | Minimum maintenance clearance - rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Top
10 | Rack-compatible footprint (600 mm wide) | Y/N | Yes
11 | Castors / levelling feet supplied | Y/N | Yes
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING - OUTDOOR UNIT
1 | Height | mm | 1245
2 | Width | mm | 1275
3 | Depth | mm | 2365
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Top / Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation - suction line | - | As per manufacturer recommendation
9 | Pipe insulation - liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | Yes
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | No
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Hot aisle containment panel kit (front cover plates) | Y/N | VS
8 | Blanking panels for empty rack-row positions | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | This full-function unit provides active dehumidification and humidity control (electric reheat + integral humidifier) - see Sections 14 and 15. Other in-row units in the room are sensible-only.
6 | Hot aisle containment is required for design intent - confirm rack layout and containment panel coordination with civil/structural.
7 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
8 | Humidifier sizing is indicative - vendor to confirm capacity meets or exceeds calculated values for site conditions.
9 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
10 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.
CR

## DST - Scheme B
TECHNICAL DATA SHEET - IN-ROW COOLER (Direct Expansion) - SCHEME B (Schneider Electric Uniflair / STULZ CyberRow or equal approved)
PROJECT: WITS - CLM DATA CENTRE ¦ REVISION: 01 ¦ DATE: 19/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all - complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception - confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R - Accept/Reject - Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | CLM-IRC-01 to 06
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 6
8 | Equipment tag numbers | - | See Dwg
9 | Warranty period | Yrs | 1
10 | Unit type | - | In-Row Cooler
11 | Redundancy configuration | - | N+1
1. ENVIRONMENTAL
1 | Site altitude | masl | 1695
2 | Air pressure at altitude (calculated) | kPa | 82.5522
3 | Air density at altitude (calculated) | kg/m³ | 0.96455
4 | Design outdoor dry-bulb temperature (summer) | °C | 37.5
5 | Design outdoor wet-bulb temperature (summer) | °C | 23.6
6 | Design outdoor dry-bulb temperature (winter) | °C | -5.1
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating - indoor unit (IEC 60529) | IP | IP20
9 | IP rating - outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class - dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE - DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 1
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 42
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | ≥0.95 (sensible-only)
12 | Unit inlet air temperature (return from hot aisle) | °C | 32
13 | Off-coil temperature (supply to cold aisle) | °C | 19
14 | Design delta T over unit (calculated) | °C | 13
15 | Unit inlet air relative humidity | % | 30
16 | Cooling efficiency (Total cooling / Total power) - EER | kWth/kW_e | ≥3.0
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT - INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Rear intake / front discharge
3 | Containment type | - | Hot aisle
4 | Airflow (design) - Q/(ρ·Cp·ΔT) | m³/s | 3.3329
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 0
8 | Total pressure drop incl. ESP | Pa | 200
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT - OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS (sensible-only - expect minimal)
Note: In-row units operate primarily on sensible load (no dehumidification) - condensate volumes are minimal. All condensate piping to be installed with minimum fall to prevent standing water.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | In-Row Cooler
2 | Pipework connection (top / side / bottom) | - | Top
3 | Dehumidification cycle | Y/N | No
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | Yes
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications - safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (CBs) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC - indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥6
11 | Temperature control method | - | Supply air temp
12 | Fan speed control method (dP between aisles / dT supply-return) | dP / dT | dP
13 | Supply of differential pressure sensors (installation by others) | Y/N | Yes
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) - min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet - BACnet/IP support | Y/N | Yes
2 | BACnet - BACnet MS/TP support | Y/N | VS
3 | BACnet - PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet - BTL listed | Y/N | VS
5 | BACnet - Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus - Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus - Modbus TCP/IP support | Y/N | VS
8 | Modbus - Register map / points list provided | Y/N | Yes
9 | SNMP - MIB file provided | Y/N | VS
10 | SNMP - Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface - 10/100/1000 Base-T | Y/N | Yes
14. HEATER REQUIREMENT (SENSIBLE-ONLY OPERATION)
In-row coolers operate sensible-only (no dehumidification cycle) - reheat is typically not required. Calculation retained for vendor confirmation if dehumidification is added.
1 | Room / cold aisle temperature setpoint | °C | 24
2 | Minimum acceptable supply air temperature | °C | 18
3 | Design airflow (from Section 4) | m³/s | 3.3329
4 | Air density at altitude (from Section 1) | kg/m³ | 0.96455
5 | Reheat duty required: Q = ρ × V̇ × Cp × (T_room - T_min_supply) | kW | 19.3846
6 | Heater type | - | PTC electric (if fitted)
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | No - sensible-only operation
15. HUMIDIFIER REQUIREMENT
Humidifier sized for worst-case winter infiltration / make-up air. In-row units may share humidification load with a dedicated make-up air unit - adjust infiltration rate per unit accordingly.
1 | Room RH setpoint (minimum) | % | 30
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 5.7
4 | Estimated infiltration / make-up air rate per unit | m³/s | 0.05
5 | Air density (from Section 1) | kg/m³ | 0.96455
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 4.39
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 × 3600 | kg/hr | 0.76219
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.57164
9 | Humidifier type | - | Electrode steam
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable - confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING - INDOOR UNIT
1 | Height | mm | 2000
2 | Width | mm | 600
3 | Depth | mm | 1146
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance - front | mm | VS
7 | Minimum maintenance clearance - rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Top
10 | Rack-compatible footprint (600 mm wide) | Y/N | Yes
11 | Castors / levelling feet supplied | Y/N | Yes
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING - OUTDOOR UNIT
1 | Height | mm | 1245
2 | Width | mm | 1275
3 | Depth | mm | 2365
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Top / Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation - suction line | - | As per manufacturer recommendation
9 | Pipe insulation - liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | No - sensible-only operation
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | No
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Hot aisle containment panel kit (front cover plates) | Y/N | VS
8 | Blanking panels for empty rack-row positions | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | In-row units handle sensible load only - no dehumidification. Latent load to be managed by dedicated make-up air or perimeter equipment.
6 | Hot aisle containment is required for design intent - confirm rack layout and containment panel coordination with civil/structural.
7 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
8 | Humidifier sizing is indicative - vendor to confirm capacity meets or exceeds calculated values for site conditions.
9 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
10 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.
CR

## DST - Full-Function - Scheme B
TECHNICAL DATA SHEET - IN-ROW COOLER (Direct Expansion) - FULL-FUNCTION UNIT - SCHEME B (Schneider Electric Uniflair / STULZ CyberRow or equal approved)
PROJECT: WITS - CLM DATA CENTRE ¦ REVISION: 01 ¦ DATE: 19/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all - complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception - confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R - Accept/Reject - Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | CLM-IRC-06
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 1
8 | Equipment tag numbers | - | CLM-IRC-06
9 | Warranty period | Yrs | 1
10 | Unit type | - | In-Row Cooler - Full-Function (Cooling + Humidity Control)
11 | Redundancy configuration | - | N/A (Standalone unit)
1. ENVIRONMENTAL
1 | Site altitude | masl | 1750
2 | Air pressure at altitude (calculated) | kPa | 81.994
3 | Air density at altitude (calculated) | kg/m³ | 0.95803
4 | Design outdoor dry-bulb temperature (summer) | °C | 37.5
5 | Design outdoor wet-bulb temperature (summer) | °C | 23.6
6 | Design outdoor dry-bulb temperature (winter) | °C | -5.1
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating - indoor unit (IEC 60529) | IP | IP20
9 | IP rating - outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class - dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE - DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 1
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 42
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | 0.75–0.85 (incl. latent load)
12 | Unit inlet air temperature (return from hot aisle) | °C | 38
13 | Off-coil temperature (supply to cold aisle) | °C | 19
14 | Design delta T over unit (calculated) | °C | 19
15 | Unit inlet air relative humidity | % | 30
16 | Cooling efficiency (Total cooling / Total power) - EER | kWth/kW_e | ≥3.0
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT - INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Rear intake / front discharge
3 | Containment type | - | Hot aisle
4 | Airflow (design) - Q/(ρ·Cp·ΔT) | m³/s | 2.2959
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 0
8 | Total pressure drop incl. ESP | Pa | 200
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT - OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS (sensible-only - expect minimal)
Note: In-row units operate primarily on sensible load (no dehumidification) - condensate volumes are minimal. All condensate piping to be installed with minimum fall to prevent standing water.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | In-Row Cooler
2 | Pipework connection (top / side / bottom) | - | Top
3 | Dehumidification cycle | Y/N | Yes
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | Yes
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications - safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (CBs) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC - indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥6
11 | Temperature control method | - | Supply air temp
12 | Fan speed control method (dP between aisles / dT supply-return) | dP / dT | dP
13 | Supply of differential pressure sensors (installation by others) | Y/N | Yes
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) - min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet - BACnet/IP support | Y/N | Yes
2 | BACnet - BACnet MS/TP support | Y/N | VS
3 | BACnet - PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet - BTL listed | Y/N | VS
5 | BACnet - Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus - Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus - Modbus TCP/IP support | Y/N | VS
8 | Modbus - Register map / points list provided | Y/N | Yes
9 | SNMP - MIB file provided | Y/N | VS
10 | SNMP - Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface - 10/100/1000 Base-T | Y/N | Yes
14. ELECTRIC REHEAT REQUIREMENT (DEHUMIDIFICATION)
Full-function unit provides active dehumidification via electric reheat downstream of the cooling coil, working with the compressor sub-cooling / reheat sequence. Vendor to confirm heater capacity meets or exceeds the calculated reheat duty below.
1 | Room / cold aisle temperature setpoint | °C | 24
2 | Minimum acceptable supply air temperature | °C | 18
3 | Design airflow (from Section 4) | m³/s | 2.2959
4 | Air density at altitude (from Section 1) | kg/m³ | 0.95803
5 | Reheat duty required: Q = ρ × V̇ × Cp × (T_room - T_min_supply) | kW | 13.2632
6 | Heater type | - | Electric resistance reheat (SCR/SSR staged control)
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | Yes
15. HUMIDIFIER REQUIREMENT
Humidifier sized for worst-case winter infiltration / make-up air for this dedicated full-function unit, which carries the room's humidification duty (integral electrode-steam humidifier).
1 | Room RH setpoint (minimum) | % | 30
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 5.7
4 | Estimated infiltration / make-up air rate per unit | m³/s | 0.05
5 | Air density (from Section 1) | kg/m³ | 0.95803
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 4.39
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 × 3600 | kg/hr | 0.75703
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.56777
9 | Humidifier type | - | Electrode steam
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable - confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING - INDOOR UNIT
1 | Height | mm | 2000
2 | Width | mm | 600
3 | Depth | mm | 1146
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance - front | mm | VS
7 | Minimum maintenance clearance - rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Top
10 | Rack-compatible footprint (600 mm wide) | Y/N | Yes
11 | Castors / levelling feet supplied | Y/N | Yes
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING - OUTDOOR UNIT
1 | Height | mm | 1245
2 | Width | mm | 1275
3 | Depth | mm | 2365
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Top / Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation - suction line | - | As per manufacturer recommendation
9 | Pipe insulation - liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | Yes
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | No
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Hot aisle containment panel kit (front cover plates) | Y/N | VS
8 | Blanking panels for empty rack-row positions | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | This full-function unit provides active dehumidification and humidity control (electric reheat + integral humidifier) - see Sections 14 and 15. Other in-row units in the room are sensible-only.
6 | Hot aisle containment is required for design intent - confirm rack layout and containment panel coordination with civil/structural.
7 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
8 | Humidifier sizing is indicative - vendor to confirm capacity meets or exceeds calculated values for site conditions.
9 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
10 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.
CR

## Extra over items (hidden)
Project:- | WITS - CLM DATA CENTRE
Project No:- | 1005297-24
Date:- | 2026-08-20
Bill:- | EXTRA OVER
Rev:- | 1899-12-31
ITEM | DESCRIPTION | UNIT | QTY | RATE
A | EXTRA OVERS
EXTRA OVER
Below items may be included in the contract at a later stage therefore rates deemed compulsory. However, total value not to be included under the total tender amount
Low Pressure Ducting Rectangular & Round Ducting including all necessary bends, spigots, fittings, galvanised duct supports, joints, fixings, vanes, hangers, supports and accessories, complete as shown on drawings, pressure tested and as per specifications.
A.1 | GALVANIZED STRAIGHT DUCTING
A.1.1 | Category 1 | sqm | Rate
A.1.2 | Category 2 | sqm | Rate
A.1.3 | Category 3 | sqm | Rate
A.1.4 | Category 4 | sqm | Rate
A.1.5 | Category 5 | sqm | Rate
A.2 | GALVANIZED ROUND DUCTING: (Category 6)
A.2.1 | Ø100 | m | Rate
A.2.2 | Ø150 | m | Rate
A.2.3 | Ø200 | m | Rate
A.2.4 | Ø250 | m | Rate
A.2.5 | Ø300 | m | Rate
A.2.6 | Ø350 | m | Rate
A.3 | INSULATED 2.5m FLEXIBLE DUCTING (ACOUSTIC) c/w JUBILEE CLAMPS:
A.3.1 | Ø150 | 1 | Rate
A.3.2 | Ø200 | 1 | Rate
A.3.3 | Ø250 | 1 | Rate
A.3.4 | Ø300 | 1 | Rate
A.3.5 | Ø350 | 1 | Rate
A.4 | UNINSULATED 2.5m FLEXIBLE DUCTING (ACOUSTIC) c/w JUBILEE CLAMPS:
A.4.1 | Ø150 | 1 | Rate
A.4.2 | Ø200 | 1 | Rate
A.4.3 | Ø250 | 1 | Rate
A.4.4 | Ø300 | 1 | Rate
A.4.5 | Ø350 | 1 | Rate
A.5 | CEILING TILES
A.5.1 | Replacement of any damaged ceiling tiles during installation - 600x1200 | 1 | Rate
ADDITIONAL ITEMS:
A.6 | Additional items shown on drawings and schematics and diagrams or in written or tabulated HVAC specification but not in BOQ and vice versa, that is necessary for a complete and fully operational and balanced system in accordance with the HVAC drawings, specifications, diagrams or schematics issued. NOTE that additional items may not be claimed at later stage by HVAC contractor, unless if the design scope changed.
A.6.1 | 1
A.6.2 | 2
A.6.3 | 3
A.6.4 | 4
A.6.5 | 5