## Summary Page
Project: | WITS - SMH DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | MASTER SUMMARY
Rev: | 2
ITEM | DESCRIPTION | AMOUNT
MASTER SUMMARY OF TENDER
1 | Preliminaries and General Items | 0
2 | DX SPLIT CRAC UNITS - SCHEME A (Stulz) | 403774.682
3 | DX SPLIT CRAC UNITS - SCHEME B (Vertiv) | 403774.682
4 | DX SPLIT CRAC UNITS - SCHEME C (Schneider) | 403774.682
Note 1: Scheme A (Stulz), Scheme B (Vertiv) and Scheme C ( Schneider) are different vendor offerings for the CRAC units, priced independently and in full on an equal footing.
Note 2: The Contractor is to complete the Technical Data Sheet attached to this BOQ for all the schemes
| TOTAL (EXCLUDING VAT) | 1211324.046
| VAT RATE | 15%
| VAT | 181698.6069
| TOTAL (INCLUDING VAT) | 1393022.6529

## Preliminaries and General Items
Project: | WITS - SMH DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | PRELIMINARIES AND GENERAL AS PER THECONDITIONS OF THE CONTRACT
Rev: | 2
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
PRELIMINARIES AND GENERAL AS PER THECONDITIONS OF THE CONTRACT
The Framework Schedule of rates is applicable to all Model
Projects and Package Orders.
FIXED PRELIMINARIES
Health and safety
1 | Plan, file and basic Mandatories (refer to Annexure 5) | Item | 1
Non-standard scaffolding
Note: Scaffolding for builderswork excluded and to be priced
during construction
2 | Scaffolding at shaft 1.5m wide x approximately 18.5m high | Item | 1
Maintenance and guarantee
3 | One year's maintenance and guarantee | Item | 1
Additional Fixed Preliminaries items
4 | Items which are not covered in the items above or in the Bill of
Quantities and falls within the Preliminaries and General
definition as per the Scope, Annexure 2 (list to be provided with
| the tender) | Item | 1
MONTHLY PRELIMINARIES
Health and safety compliance including Part-time Health and
Safety Officer (cost per month)
Note: Tenderers to only price applicable item for the Model
project.
5 | Cost per month where Total of the Prices is R 0 to R 2 million
| ONLY WHEN high-risk factors are applicable | Mnth | 3
6 | Cost per month where Total of the Prices is R 2 million to R 5
| million | Mnth | 3
7 | Cost per month where Total of the Prices is R 5 million to R 20
| million | Mnth | 3
Additional Monthly Preliminaries items
8 | Items which are not covered in the items above or in the Bill of
Quantities and falls within the Preliminaries and General
definition as per the Scope, Annexure 2 (list to be provided with
| the tender) | Item | 1
EQUIPMENT
Site enclosure, hoarding, temporary screens, etc.
9 | 1.80m High galvanised diamond mesh fence tied to and
including galvanised posts, stays, etc. fixed in ground and
| covered with 50% green shade cloth | m | 40
10 | 900 x 1 800mm High single gate to suit fencing and covered
with galvanised wire mesh and 50% shade cloth, including
hinges, heavy duty lockable barrel bolt and 51mm "Union 3122"
| padlock | No | 1
11 | 6 000 x 1 800mm High double leaf gate covered with
galvanised wire mesh and 50% shade cloth, including hinges,
heavy duty lockable barrel bolt and 51mm "Union 3122"
| padlock | No |  |  | Rate only
12 | Drywall barricade 2.7m high of galvanised steel channel section
rails and studs covered on one side with 12,5mm gypsum
plasterboard and finished with two coats interior quality PVA
| emulsion paint, including corners, ends, etc. | m | 20
13 | Extra over preceding item for hollow core single door 813 x
2032mm high, including steel frame, two-lever mortice lock,
| primer and two coats paint | No | 1
Additional Equipment Preliminaries items
14 | Items which are not covered in the items above or in the Bill of
Quantities and falls within the Preliminaries and General
definition as per the Scope, Annexure 2 (list to be provided with
| the tender) | Item | 1

## CRAC Units - Scheme A
Project: | WITS - SMH DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX SPLIT CRAC UNITS - SCHEME A (Stulz)
Rev: | 2
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX CRAC UNITS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion CRAC units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the contractor for site conditions (1750 masl, ambient per specification). INDOOR UNITS per specification including: unit-mounted controllers c/w wiring, filters and filter frames, condensate drain pumps (if required), connection to electrical isolator within 1 m of equipment (provided adjacent, by others), and all required accessories. OUTDOOR UNITS per specification including: galvanised/anti-corrosion wall mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR CRAC UNITS - Supply & Install
2.1.1 | CRAC indoor units - SMH-CRAC-06, SMH-CRAC-07, SMH-CRAC-08. Total net cooling capacity = 63 kW, sensible 58.6 kW (derated for 1 750 masl); Stulz ASD 672 A or approved equivalent. Complete with factory-fitted E²-controller, EC fans, EEV, dual A/B power feeds and ATS as per TDS. Confirm unit model against TDS before tender issue. | no | 3 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - suitably selected for unit operating weight | no | 3 |  | 0
2.1.3 | Base frame / floor stand, 400 mm high, powder-coated steel, suitable for raised floor installation | no | 3 |  | 0
2.1.4 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover (total 6 sets) | set | 6 |  | 0
2.1.5 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 6 |  | 0
2.1.6 | S-trap condensate drain connection - fabricated and fitted | no | 3 |  | 0
2.1.7 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 3 |  | 0
2.1.8 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 3 |  | 0
2.1.9 | Drip tray under unit footprint (secondary containment) - optional | no | 3 |  | 0
2.1.10 | Electric reheat battery/heater, 20 kW capacity per unit, factory-fitted or field-installed c/w controls, contactors and high-limit safety cut-out, supplied and installed complete | no | 3 |  | 0
2.1.11 | Humidifier (steam/adiabatic type), 0.56 kg/h capacity per unit, c/w water supply connection, drain and control interface, supplied and installed complete | no | 3 |  | 0
2.1.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.13 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor Units |  |  | Subtotal | 0
2.2 | OUTDOOR CONDENSER UNITS - Supply & Install
2.2.1 | Condenser units - SMH-CND-06, SMH-CND-07, SMH-CND-08. Matched to indoor units, EC condenser fans, IP65 minimum, derated for 1750 masl ambient | no | 3 |  | 0
2.2.2 | Steel frame for condensing units c/w TICO pads / vibration isolators(400mm height each) | no | 3 |  | 0
2.2.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 3 |  | 0
2.2.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 3 |  | 0
2.2.5 | Plinth / housekeeping pad for outdoor unit base (concrete, 100 mm above FFL) | no | 3 |  | 0
2.2.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Outdoor Units |  |  | Subtotal | 0
2.3 | REFRIGERANT PIPING SYSTEM
2.3.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), copper - referenced on the specifications attached on tender pack, including bends, joints and brazed connections | m | 90 |  | 0
2.3.2 | Open cable trays for piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer | m | 90 |  | 0
2.3.3 | Service / isolation valves on refrigerant lines (per circuit) | set | 3 |  | 0
2.3.4 | Filter drier (one per circuit) | no | 3 |  | 0
2.3.5 | Sight glass with moisture indicator (one per circuit) | no | 3 |  | 0
2.3.6 | Oil trap / U-bend for long vertical runs (where applicable) | no | 3 |  | 0
2.3.7 | Pipe identification labels and flow-direction arrows | set | 3 |  | 0
2.3.8 | Insulation for new refrigerant piping | m | 90 |  | 0
2.3.9 | Insulation for EXISTING refrigerant piping (re-insulation of existing run) GAS OUTSIDE DIAMETER 25.4 mm | m | 75 |  | 0
2.3.10 | Insulation for EXISTING refrigerant piping (re-insulation of existing run) Liquid OUTSIDE DIAMETER 22.2 mm | m | 75 |  | 0
2.3.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Refrigerant Piping |  |  | Subtotal | 0
2.4 | CONDENSATE DRAINAGE SYSTEM
2.4.1 | Condensate drain piping c/w S-trap, to full bore drain point | m | 20 |  | 0
2.4.2 | Overflow alarm wired back to unit controls | no | 3 |  | 0
2.4.3 | Insulation on condensate pipework (to prevent sweating) | m | 30 |  | 0
2.4.4 | Pipe supports, brackets and clips for condensate piping | m | 30 |  | 0
2.4.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Condensate Drainage |  |  | Subtotal | 0
2.5 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX CRAC units and fans, including DBs, local starter / isolator, controls etc. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories.
2.5.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit ATS terminals) c/w cable tray | m | 3 |  | 0
2.5.2 | Electrical cable reticulation - Outdoor Unit (from isolator to condenser) c/w cable tray | m | 90 |  | 0
2.5.3 | Dual Power Source Selector (ATS) - fitted on to indoor unit | no | 6 |  | 0
2.5.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Electrical |  |  | Subtotal | 0
2.6 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.6.1 | BACnet IP interface card per unit - as specified | no | 3 |  | 0
2.6.2 | Unit-to-unit interlink cabling for master/slave supervisory operation (per manufacturer) | no | 3 |  | 0
2.6.3 | Remote temperature (return air / cold aisle / supply) | no | 3 |  | 0
2.6.4 | RH sensors (return air / cold aisle / supply) |  | 3 |  | 0
2.6.5 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.6.6 | BACnet points list verification & integration testing with site BMS | no | 1 |  | 0
2.6.7 | BMS graphics development and integration on site head-end (3 units) | Sum | 1 |  | 0
2.6.8 | Controls commissioning, sensor calibration, alarm verification, set-point handover | Sum | 1 |  | 0
2.6.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Controls & BMS |  |  | Subtotal | 0
2.7 | BMS - EXISTING CRAC UNIT INTEGRATION & REMOTE MONITORING PLATFORM
2.7.1 | Survey and audit of all EXISTING CRAC units on site - establish control protocol per unit (BACnet IP/MSTP, Modbus RTU/TCP, LON, proprietary or other), document firmware version, available I/O points, and interface requirements. Submit audit report for consultant approval before proceeding with integration. | Sum | 1 |  | 0
2.7.2 | BMS points list compilation for existing units - minimum points: supply air temp, return air temp, setpoint, compressor status, fan speed, alarm summary, power consumption (if available). Submit to consultant for approval prior to integration. | Sum | 1 |  | 0
2.7.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - BMS Existing Unit Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Core drilling through walls for pipe and cable penetrations (75-150 mm) |  |  |  | Included in the provisional sum below
2.8.2 | Making good of penetrations, plastering and finishing to existing standard
2.8.3 | Concrete plinths / housekeeping pads for outdoor units (200 mm thick, reinforced)
2.8.4 | Waterproofing / sealant repairs around outdoor unit base
2.8.5 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate)
2.8.6 | Additional item necessary for completion - contractor to describe
2.8.7 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work (Provisional sum) |  |  | Subtotal | 403774.682
2.9 | TESTING & COMMISSIONING
2.9.1 | Refrigerant pressure test certificate per circuit (nitrogen) - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.2 | Performance testing - measured capacity, EER, SFP - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.3 | Air balance testing - supply / return airflows, velocity over coil <2.5 m/s | no | 3 |  | 0
2.9.4 | Air rebalancing of cold-aisle floor grilles after CRAC installation | no | 120
2.9.5 | Noise level testing - Lp @ 2 m measurement - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.6 | Functional Testing | no | 3 |  | 0
2.9.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.9.8 | Nitrogen pressure test (≥40 bar holding for 24 hr) - certificate per circuit | no | 3 |  | 0
2.9.9 | Vacuum / dehydration to <500 microns including standing test | no | 3 |  | 0
2.9.10 | Commissioning report, signed | no | 3 |  | 0
2.9.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Testing & Commissioning |  |  | Subtotal | 0
2.10 | SPARES & RECOMMENDED CONSUMABLES
2.10.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.10.2 | Supplier to submit list
2.10.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Spares |  |  | Subtotal | 0
2.11 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation of the DX CRAC system. NOTE: Additional items may NOT be claimed at a later stage by the Contractor unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities for tender clarity.
2.11.1 |  |  |  |  | 0
2.11.2 |  |  |  |  | 0
2.11.3 |  |  |  |  | 0
2.11.4 |  |  |  |  | 0
2.11.5 |  |  |  |  | 0
2.11.6 |  |  |  |  | 0
2.11.7 |  |  |  |  | 0
2.11.8 |  |  |  |  | 0
| Subtotal 2.11 - Additional Items |  |  | Subtotal | 0
| BILL 2 - DX CRAC UNITS |  |  | SUB-TOTAL | 403774.682
Carried forward to Summary Page →

## DST - Scheme A
TECHNICAL DATA SHEET — CRAC UNIT (Direct Expansion) — SCHEME A (STULZ)
PROJECT: WITS - SMH DATA CENTRE ¦ SCHEME: A (STULZ) ¦ REVISION: 01 ¦ DATE: 22/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all — complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception — confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R — Accept/Reject — Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | SMH-CRAC-06/07/08
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 3
8 | Equipment tag numbers | - | See Dwg
9 | Warranty period | Yrs | 1
10 | Unit type | - | CRAC - Downblow
11 | Redundancy configuration | - | N/A
1. ENVIRONMENTAL
1 | Site altitude | masl | 1750
2 | Air pressure at altitude (calculated) | kPa | 81.994
3 | Air density at altitude (calculated) | kg/m³ | 0.95803
4 | Design outdoor dry-bulb temperature (summer) | °C | 37
5 | Design outdoor wet-bulb temperature (summer) | °C | 21.9
6 | Design outdoor dry-bulb temperature (winter) | °C | 1.6
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating — indoor unit (IEC 60529) | IP | IP20
9 | IP rating — outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class — dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE — DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 2
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 58.6
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | ≥0.90
12 | Unit inlet air temperature (return air) | °C | 34
13 | Off-coil temperature | °C | 20
14 | Design delta T over unit (calculated) | °C | 14
15 | Unit inlet air relative humidity | % | 26.3
16 | Cooling efficiency (Total cooling / Total power) — EER | kWth/kW_e | ≥3.5
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT — INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Down blow, top return
3 | Containment type | - | Cold aisle
4 | Airflow (design) | m³/s | 4.3474
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 80
8 | Total pressure drop incl. ESP | Pa | VS
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT — OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS
Note: All condensate piping to be installed with minimum fall to prevent standing water. Insulation required below raised floor.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | CRAC
2 | Pipework connection (top / side / bottom) | - | Bottom
3 | Dehumidification cycle | Y/N | Yes
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | VS
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications — safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (circuit breakers) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC — indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥5
11 | Temperature control method | - | Off coil temp
12 | Fan speed control method | dP / dT | dT
13 | Supply of differential pressure sensors (installation by others) | Y/N | No
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) — min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet — BACnet/IP support | Y/N | Yes
2 | BACnet — BACnet MS/TP support | Y/N | VS
3 | BACnet — PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet — BTL listed | Y/N | VS
5 | BACnet — Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus — Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus — Modbus TCP/IP support | Y/N | VS
8 | Modbus — Register map / points list provided | Y/N | Yes
9 | SNMP — MIB file provided | Y/N | VS
10 | SNMP — Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface — 10/100/1000 Base-T | Y/N | Yes
14. HEATER REQUIREMENT (WINTER REHEAT)
Heater required when return air absolute humidity>10.75g/kg and the unit has to dehumidify to the upper absolute humidity and overcools below supply air
1 | CRAC temperature setpoint | °C | 20
2 | Minimum acceptable supply air temperature | °C | 15
3 | Design airflow (from Section 4) | m³/s | 4.3474
4 | Air density at altitude (from Section 1) | kg/m³ | 0.95803
5 | Reheat duty required: Q = ρ × V̇ × Cp × (T_room - T_min_supply) | kW | 20.9286
6 | Heater type | - | PTC electric
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | Yes
15. HUMIDIFIER REQUIREMENT
Humidifier required when return air humidity drops below setpoint. Sized for worst-case winter infiltration / make-up air scenario.
1 | Room RH setpoint (minimum) | % | 12.1
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 2.4
4 | Estimated infiltration / make-up air rate | m³/s | 0.15
5 | Air density (from Section 1) | kg/m³ | 0.95803
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 1.09
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 | kg/hr | 0.56389
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.42292
9 | Humidifier type | - | Adiabatic Humidifier
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable — confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING — INDOOR UNIT
1 | Height (excl. fan box) | mm | 986
2 | Width | mm | 3660
3 | Depth | mm | 920
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance — front | mm | VS
7 | Minimum maintenance clearance — rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Bottom
10 | Raised floor installation | Y/N | No
11 | Raised floor tile cutout dimensions (W × D) | mm | VS
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING — OUTDOOR UNIT
1 | Height | mm | 1980
2 | Width | mm | 1750
3 | Depth | mm | 890
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation — suction line | - | As per manufacturer recommendation
9 | Pipe insulation — liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | Yes
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | Yes
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Caster wheels for positioning | Y/N | VS
8 | Louvred floor tile(s) supplied | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | Condensate piping specification applies from the unit drain stub to the nearest building drain point.
6 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
7 | Heater and humidifier sizing is indicative — vendor to confirm capacity meets or exceeds calculated values.
8 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
9 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.

## CRAC Units - Scheme B
Project: | WITS - SMH DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX SPLIT CRAC UNITS - SCHEME B (Vertiv)
Rev: | 2
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX CRAC UNITS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion CRAC units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the contractor for site conditions (1750 masl, ambient per specification). INDOOR UNITS per specification including: unit-mounted controllers c/w wiring, filters and filter frames, condensate drain pumps (if required), connection to electrical isolator within 1 m of equipment (provided adjacent, by others), and all required accessories. OUTDOOR UNITS per specification including: galvanised/anti-corrosion wall mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR CRAC UNITS - Supply & Install
2.1.1 | CRAC indoor units - SMH-CRAC-06, SMH-CRAC-07, SMH-CRAC-08. Total net cooling capacity = 63 kW, sensible 58.6 kW (derated for 1 750 masl); Vertiv. Complete with EC fans, EEV, dual A/B power feeds and ATS as per TDS. Confirm unit model against TDS before tender issue. | no | 3 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - suitably selected for unit operating weight | no | 3 |  | 0
2.1.3 | Base frame / floor stand, 400 mm high, powder-coated steel, suitable for raised floor installation | no | 3 |  | 0
2.1.4 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover (total 6 sets) | set | 6 |  | 0
2.1.5 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 6 |  | 0
2.1.6 | S-trap condensate drain connection - fabricated and fitted | no | 3 |  | 0
2.1.7 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 3 |  | 0
2.1.8 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 3 |  | 0
2.1.9 | Drip tray under unit footprint (secondary containment) - optional | no | 3 |  | 0
2.1.10 | Electric reheat battery/heater, 20 kW capacity per unit, factory-fitted or field-installed c/w controls, contactors and high-limit safety cut-out, supplied and installed complete | no | 3 |  | 0
2.1.11 | Humidifier (steam/adiabatic type), 0.56 kg/h capacity per unit, c/w water supply connection, drain and control interface, supplied and installed complete | no | 3 |  | 0
2.1.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.13 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor Units |  |  | Subtotal | 0
2.2 | OUTDOOR CONDENSER UNITS - Supply & Install
2.2.1 | Condenser units - SMH-CND-06, SMH-CND-07, SMH-CND-08. Matched to indoor units, EC condenser fans, IP65 minimum, derated for 1750 masl ambient | no | 3 |  | 0
2.2.2 | Steel frame for condensing units c/w TICO pads / vibration isolators(400mm height each) | no | 3 |  | 0
2.2.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 3 |  | 0
2.2.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 3 |  | 0
2.2.5 | Plinth / housekeeping pad for outdoor unit base (concrete, 100 mm above FFL) | no | 3 |  | 0
2.2.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Outdoor Units |  |  | Subtotal | 0
2.3 | REFRIGERANT PIPING SYSTEM
2.3.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), copper - referenced on the specifications attached on tender pack, including bends, joints and brazed connections | m | 90 |  | 0
2.3.2 | Open cable trays for piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer | m | 90 |  | 0
2.3.3 | Service / isolation valves on refrigerant lines (per circuit) | set | 3 |  | 0
2.3.4 | Filter drier (one per circuit) | no | 3 |  | 0
2.3.5 | Sight glass with moisture indicator (one per circuit) | no | 3 |  | 0
2.3.6 | Oil trap / U-bend for long vertical runs (where applicable) | no | 3 |  | 0
2.3.7 | Pipe identification labels and flow-direction arrows | set | 3 |  | 0
2.3.8 | Insulation for new refrigerant piping | m | 90 |  | 0
2.3.9 | Insulation for EXISTING refrigerant piping (re-insulation of existing run) GAS OUTSIDE DIAMETER 25.4 mm | m | 75 |  | 0
2.3.10 | Insulation for EXISTING refrigerant piping (re-insulation of existing run) Liquid OUTSIDE DIAMETER 22.2 mm | m | 75 |  | 0
2.3.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Refrigerant Piping |  |  | Subtotal | 0
2.4 | CONDENSATE DRAINAGE SYSTEM
2.4.1 | Condensate drain piping c/w S-trap, to full bore drain point | m | 20 |  | 0
2.4.2 | Overflow alarm wired back to unit controls | no | 3 |  | 0
2.4.3 | Insulation on condensate pipework (to prevent sweating) | m | 30 |  | 0
2.4.4 | Pipe supports, brackets and clips for condensate piping | m | 30 |  | 0
2.4.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Condensate Drainage |  |  | Subtotal | 0
2.5 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX CRAC units and fans, including DBs, local starter / isolator, controls etc. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories.
2.5.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit ATS terminals) c/w cable tray | m | 3 |  | 0
2.5.2 | Electrical cable reticulation - Outdoor Unit (from isolator to condenser) c/w cable tray | m | 90 |  | 0
2.5.3 | Dual Power Source Selector (ATS) - fitted on to indoor unit | no | 6 |  | 0
2.5.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Electrical |  |  | Subtotal | 0
2.6 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.6.1 | BACnet IP interface card per unit - as specified | no | 3 |  | 0
2.6.2 | Unit-to-unit interlink cabling for master/slave supervisory operation (per manufacturer) | no | 3 |  | 0
2.6.3 | Remote temperature (return air / cold aisle / supply) | no | 3 |  | 0
2.6.4 | RH sensors (return air / cold aisle / supply) |  | 3 |  | 0
2.6.5 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.6.6 | BACnet points list verification & integration testing with site BMS | no | 1 |  | 0
2.6.7 | BMS graphics development and integration on site head-end (3 units) | Sum | 1 |  | 0
2.6.8 | Controls commissioning, sensor calibration, alarm verification, set-point handover | Sum | 1 |  | 0
2.6.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Controls & BMS |  |  | Subtotal | 0
2.7 | BMS - EXISTING CRAC UNIT INTEGRATION & REMOTE MONITORING PLATFORM
2.7.1 | Survey and audit of all EXISTING CRAC units on site - establish control protocol per unit (BACnet IP/MSTP, Modbus RTU/TCP, LON, proprietary or other), document firmware version, available I/O points, and interface requirements. Submit audit report for consultant approval before proceeding with integration. | Sum | 1 |  | 0
2.7.2 | BMS points list compilation for existing units - minimum points: supply air temp, return air temp, setpoint, compressor status, fan speed, alarm summary, power consumption (if available). Submit to consultant for approval prior to integration. | Sum | 1 |  | 0
2.7.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - BMS Existing Unit Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Core drilling through walls for pipe and cable penetrations (75-150 mm) |  |  |  | Included in the provisional sum below
2.8.2 | Making good of penetrations, plastering and finishing to existing standard
2.8.3 | Concrete plinths / housekeeping pads for outdoor units (200 mm thick, reinforced)
2.8.4 | Waterproofing / sealant repairs around outdoor unit base
2.8.5 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate)
2.8.6 | Additional item necessary for completion - contractor to describe
2.8.7 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work (Provisional sum) |  |  | Subtotal | 403774.682
2.9 | TESTING & COMMISSIONING
2.9.1 | Refrigerant pressure test certificate per circuit (nitrogen) - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.2 | Performance testing - measured capacity, EER, SFP - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.3 | Air balance testing - supply / return airflows, velocity over coil <2.5 m/s | no | 3 |  | 0
2.9.4 | Air rebalancing of cold-aisle floor grilles after CRAC installation | no | 120 |  | 0
2.9.5 | Noise level testing - Lp @ 2 m measurement - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.6 | Functional Testing | no | 3 |  | 0
2.9.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.9.8 | Nitrogen pressure test (≥40 bar holding for 24 hr) - certificate per circuit | no | 3 |  | 0
2.9.9 | Vacuum / dehydration to <500 microns including standing test | no | 3 |  | 0
2.9.10 | Commissioning report, signed | no | 3 |  | 0
2.9.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Testing & Commissioning |  |  | Subtotal | 0
2.10 | SPARES & RECOMMENDED CONSUMABLES
2.10.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.10.2 | Supplier to submit list
2.10.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Spares |  |  | Subtotal | 0
2.11 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation of the DX CRAC system. NOTE: Additional items may NOT be claimed at a later stage by the Contractor unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities for tender clarity.
2.11.1 |  |  |  |  | 0
2.11.2 |  |  |  |  | 0
2.11.3 |  |  |  |  | 0
2.11.4 |  |  |  |  | 0
2.11.5 |  |  |  |  | 0
2.11.6 |  |  |  |  | 0
2.11.7 |  |  |  |  | 0
2.11.8 |  |  |  |  | 0
| Subtotal 2.11 - Additional Items |  |  | Subtotal | 0
| BILL 2 - DX CRAC UNITS |  |  | SUB-TOTAL | 403774.682
Carried forward to Summary Page →

## DST - Scheme B
TECHNICAL DATA SHEET — CRAC UNIT (Direct Expansion) — SCHEME B (VERTIV)
PROJECT: WITS - SMH DATA CENTRE ¦ SCHEME: B (VERTIV) ¦ REVISION: 01 ¦ DATE: 22/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all — complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception — confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R — Accept/Reject — Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | SMH-CRAC-06/07/08
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 3
8 | Equipment tag numbers | - | See Dwg
9 | Warranty period | Yrs | 1
10 | Unit type | - | CRAC - Downblow
11 | Redundancy configuration | - | N/A
1. ENVIRONMENTAL
1 | Site altitude | masl | 1750
2 | Air pressure at altitude (calculated) | kPa | 81.994
3 | Air density at altitude (calculated) | kg/m³ | 0.95803
4 | Design outdoor dry-bulb temperature (summer) | °C | 37
5 | Design outdoor wet-bulb temperature (summer) | °C | 21.9
6 | Design outdoor dry-bulb temperature (winter) | °C | 1.6
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating — indoor unit (IEC 60529) | IP | IP20
9 | IP rating — outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class — dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE — DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 2
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 58.6
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | ≥0.90
12 | Unit inlet air temperature (return air) | °C | 34
13 | Off-coil temperature | °C | 20
14 | Design delta T over unit (calculated) | °C | 14
15 | Unit inlet air relative humidity | % | 26.3
16 | Cooling efficiency (Total cooling / Total power) — EER | kWth/kW_e | ≥3.5
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT — INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Down blow, top return
3 | Containment type | - | Cold aisle
4 | Airflow (design) | m³/s | 4.3474
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 80
8 | Total pressure drop incl. ESP | Pa | VS
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT — OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS
Note: All condensate piping to be installed with minimum fall to prevent standing water. Insulation required below raised floor.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | CRAC
2 | Pipework connection (top / side / bottom) | - | Bottom
3 | Dehumidification cycle | Y/N | Yes
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | VS
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications — safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (circuit breakers) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC — indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥5
11 | Temperature control method | - | Off coil temp
12 | Fan speed control method | dP / dT | dT
13 | Supply of differential pressure sensors (installation by others) | Y/N | No
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) — min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet — BACnet/IP support | Y/N | Yes
2 | BACnet — BACnet MS/TP support | Y/N | VS
3 | BACnet — PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet — BTL listed | Y/N | VS
5 | BACnet — Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus — Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus — Modbus TCP/IP support | Y/N | VS
8 | Modbus — Register map / points list provided | Y/N | Yes
9 | SNMP — MIB file provided | Y/N | VS
10 | SNMP — Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface — 10/100/1000 Base-T | Y/N | Yes
14. HEATER REQUIREMENT (WINTER REHEAT)
Heater required when return air absolute humidity>10.75g/kg and the unit has to dehumidify to the upper absolute humidity and overcools below supply air
1 | CRAC temperature setpoint | °C | 20
2 | Minimum acceptable supply air temperature | °C | 15
3 | Design airflow (from Section 4) | m³/s | 4.3474
4 | Air density at altitude (from Section 1) | kg/m³ | 0.95803
5 | Reheat duty required: Q = ρ × V̇ × Cp × (T_room - T_min_supply) | kW | 20.9286
6 | Heater type | - | PTC electric
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | Yes
15. HUMIDIFIER REQUIREMENT
Humidifier required when return air humidity drops below setpoint. Sized for worst-case winter infiltration / make-up air scenario.
1 | Room RH setpoint (minimum) | % | 12.1
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 2.4
4 | Estimated infiltration / make-up air rate | m³/s | 0.15
5 | Air density (from Section 1) | kg/m³ | 0.95803
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 1.09
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 | kg/hr | 0.56389
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.42292
9 | Humidifier type | - | Adiabatic Humidifier
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable — confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING — INDOOR UNIT
1 | Height (excl. fan box) | mm | 986
2 | Width | mm | 3660
3 | Depth | mm | 920
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance — front | mm | VS
7 | Minimum maintenance clearance — rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Bottom
10 | Raised floor installation | Y/N | No
11 | Raised floor tile cutout dimensions (W × D) | mm | VS
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING — OUTDOOR UNIT
1 | Height | mm | 1980
2 | Width | mm | 1750
3 | Depth | mm | 890
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation — suction line | - | As per manufacturer recommendation
9 | Pipe insulation — liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | Yes
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | Yes
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Caster wheels for positioning | Y/N | VS
8 | Louvred floor tile(s) supplied | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | Condensate piping specification applies from the unit drain stub to the nearest building drain point.
6 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
7 | Heater and humidifier sizing is indicative — vendor to confirm capacity meets or exceeds calculated values.
8 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
9 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.

## CRAC Units - Scheme C
Project: | WITS - SMH DATA CENTRE
Project No: | 1005297-24
Date: | 2026-08-20
Bill: | DX SPLIT CRAC UNITS - SCHEME C (Schneider Uniflair)
Rev: | 2
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
2 | DX CRAC UNITS - SUPPLY, INSTALL, TEST & COMMISSION
New direct-expansion CRAC units, supplied, tested and installed in position in accordance with the Technical Data Sheet and Specification attached to this tender package. Including refrigerant piping, all necessary trunking, electrical connections, control wiring, hard-wired remote controllers, labelling, hail-guards, unit-strut brackets and all mounting accessories. All figures to be derated by the contractor for site conditions (1750 masl, ambient per specification). INDOOR UNITS per specification including: unit-mounted controllers c/w wiring, filters and filter frames, condensate drain pumps (if required), connection to electrical isolator within 1 m of equipment (provided adjacent, by others), and all required accessories. OUTDOOR UNITS per specification including: galvanised/anti-corrosion wall mounts, brackets, fasteners, vibration pads, controller box, connection to electrical isolator within 1 m, expansion valves, piping, adapters and all items required for a complete installation capable of the design intent.
2.1 | INDOOR CRAC UNITS - Supply & Install
2.1.1 | CRAC indoor units - SMH-CRAC-06, SMH-CRAC-07, SMH-CRAC-08. Total net cooling capacity = 63 kW, sensible 58.6 kW (derated for 1 750 masl); Schneider Uniflair. Complete with EC fans, EEV, dual A/B power feeds and ATS as per TDS. Confirm unit model against TDS before tender issue. | no | 3 |  | 0
2.1.2 | Anti-vibration mounts (AVM) / TICO pads - suitably selected for unit operating weight | no | 3 |  | 0
2.1.3 | Base frame / floor stand, 400 mm high, powder-coated steel, suitable for raised floor installation | no | 3 |  | 0
2.1.4 | Filter sets per unit - one set for commissioning PLUS one additional set installed at handover (total 6 sets) | set | 6 |  | 0
2.1.5 | Refrigerant leak detection sensor (onboard or remote rope-type per TDS) | no | 6 |  | 0
2.1.6 | S-trap condensate drain connection - fabricated and fitted | no | 3 |  | 0
2.1.7 | Unit-mounted HMI controller c/w wiring, terminations and configuration | no | 3 |  | 0
2.1.8 | Equipment labelling - engraved Traffolyte labels, asset tags, schematic identification | no | 3 |  | 0
2.1.9 | Drip tray under unit footprint (secondary containment) - optional | no | 3 |  | 0
2.1.10 | Electric reheat battery/heater, 20 kW capacity per unit, factory-fitted or field-installed c/w controls, contactors and high-limit safety cut-out, supplied and installed complete | no | 3 |  | 0
2.1.11 | Humidifier (steam/adiabatic type), 0.56 kg/h capacity per unit, c/w water supply connection, drain and control interface, supplied and installed complete | no | 3 |  | 0
2.1.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.1.13 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.1 - Indoor Units |  |  | Subtotal | 0
2.2 | OUTDOOR CONDENSER UNITS - Supply & Install
2.2.1 | Condenser units - SMH-CND-06, SMH-CND-07, SMH-CND-08. Matched to indoor units, EC condenser fans, IP65 minimum, derated for 1750 masl ambient | no | 3 |  | 0
2.2.2 | Steel frame for condensing units c/w TICO pads / vibration isolators(400mm height each) | no | 3 |  | 0
2.2.3 | Hail guards (galvanised steel mesh) fitted to condenser coil face | no | 3 |  | 0
2.2.4 | Mounts / brackets - galvanised or anti-corrosion treated, fasteners included | set | 3 |  | 0
2.2.5 | Plinth / housekeeping pad for outdoor unit base (concrete, 100 mm above FFL) | no | 3 |  | 0
2.2.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.2.7 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.2 - Outdoor Units |  |  | Subtotal | 0
2.3 | REFRIGERANT PIPING SYSTEM
2.3.1 | Refrigerant piping between indoor and outdoor units (gas + liquid line), copper - referenced on the specifications attached on tender pack, including bends, joints and brazed connections | m | 90 |  | 0
2.3.2 | Open cable trays for piping and condenser power including pipe brackets, supports and hangers - galvanised, spaced per manufacturer | m | 90 |  | 0
2.3.3 | Service / isolation valves on refrigerant lines (per circuit) | set | 3 |  | 0
2.3.4 | Filter drier (one per circuit) | no | 3 |  | 0
2.3.5 | Sight glass with moisture indicator (one per circuit) | no | 3 |  | 0
2.3.6 | Oil trap / U-bend for long vertical runs (where applicable) | no | 3 |  | 0
2.3.7 | Pipe identification labels and flow-direction arrows | set | 3 |  | 0
2.3.8 | Insulation for new refrigerant piping | m | 90 |  | 0
2.3.9 | Insulation for EXISTING refrigerant piping (re-insulation of existing run) GAS OUTSIDE DIAMETER 25.4 mm | m | 75 |  | 0
2.3.10 | Insulation for EXISTING refrigerant piping (re-insulation of existing run) Liquid OUTSIDE DIAMETER 22.2 mm | m | 75 |  | 0
2.3.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.3.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.3 - Refrigerant Piping |  |  | Subtotal | 0
2.4 | CONDENSATE DRAINAGE SYSTEM
2.4.1 | Condensate drain piping c/w S-trap, to full bore drain point | m | 20 |  | 0
2.4.2 | Overflow alarm wired back to unit controls | no | 3 |  | 0
2.4.3 | Insulation on condensate pipework (to prevent sweating) | m | 30 |  | 0
2.4.4 | Pipe supports, brackets and clips for condensate piping | m | 30 |  | 0
2.4.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.4.6 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.4 - Condensate Drainage |  |  | Subtotal | 0
2.5 | ELECTRICAL INSTALLATION
Electrical installation and wiring, complete for all DX CRAC units and fans, including DBs, local starter / isolator, controls etc. Supply, install and commission for use c/w breakers, isolators, contactors, relays, all necessary cables, connections and accessories.
2.5.1 | Electrical cable reticulation - Indoor Unit (from isolator to unit ATS terminals) c/w cable tray | m | 3 |  | 0
2.5.2 | Electrical cable reticulation - Outdoor Unit (from isolator to condenser) c/w cable tray | m | 90 |  | 0
2.5.3 | Dual Power Source Selector (ATS) - fitted on to indoor unit | no | 6 |  | 0
2.5.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.5.5 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.5 - Electrical |  |  | Subtotal | 0
2.6 | CONTROLS, INSTRUMENTATION & BMS INTEGRATION
2.6.1 | BACnet IP interface card per unit - as specified | no | 3 |  | 0
2.6.2 | Unit-to-unit interlink cabling for master/slave supervisory operation (per manufacturer) | no | 3 |  | 0
2.6.3 | Remote temperature(return air / cold aisle / supply) | no | 3 |  | 0
2.6.4 | RH sensors (return air / cold aisle / supply) |  | 3 |  | 0
2.6.5 | Network cabling - Cat 6, terminated and tested (BMS / HMI / interlinks) | m | 80 |  | 0
2.6.6 | BACnet points list verification & integration testing with site BMS | no | 1 |  | 0
2.6.7 | BMS graphics development and integration on site head-end (3 units) | Sum | 1 |  | 0
2.6.8 | Controls commissioning, sensor calibration, alarm verification, set-point handover | Sum | 1 |  | 0
2.6.9 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.6.10 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.6 - Controls & BMS |  |  | Subtotal | 0
2.7 | BMS - EXISTING CRAC UNIT INTEGRATION & REMOTE MONITORING PLATFORM
2.7.1 | Survey and audit of all EXISTING CRAC units on site - establish control protocol per unit (BACnet IP/MSTP, Modbus RTU/TCP, LON, proprietary or other), document firmware version, available I/O points, and interface requirements. Submit audit report for consultant approval before proceeding with integration. | Sum | 1 |  | 0
2.7.2 | BMS points list compilation for existing units - minimum points: supply air temp, return air temp, setpoint, compressor status, fan speed, alarm summary, power consumption (if available). Submit to consultant for approval prior to integration. | Sum | 1 |  | 0
2.7.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.7.4 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.7 - BMS Existing Unit Integration |  |  | Subtotal | 0
2.8 | BUILDERS WORK & CIVILS
2.8.1 | Core drilling through walls for pipe and cable penetrations (75-150 mm) |  |  |  | Included in the provisional sum below
2.8.2 | Making good of penetrations, plastering and finishing to existing standard
2.8.3 | Concrete plinths / housekeeping pads for outdoor units (200 mm thick, reinforced)
2.8.4 | Waterproofing / sealant repairs around outdoor unit base
2.8.5 | Fire-stopping at fire-rated penetrations (intumescent sealant + certificate)
2.8.6 | Additional item necessary for completion - contractor to describe
2.8.7 | Additional item necessary for completion - contractor to describe
| Subtotal 2.8 - Builders Work (Provisional sum) |  |  | Subtotal | 403774.682
2.9 | TESTING & COMMISSIONING
2.9.1 | Refrigerant pressure test certificate per circuit (nitrogen) - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.2 | Performance testing - measured capacity, EER, SFP - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.3 | Air balance testing - supply / return airflows, velocity over coil <2.5 m/s | no | 3 |  | 0
2.9.4 | Air rebalancing of cold-aisle floor grilles after CRAC installation | no | 120 |  | 0
2.9.5 | Noise level testing - Lp @ 2 m measurement - referenced on the specifications attached on tender pack | no | 3 |  | 0
2.9.6 | Functional Testing | no | 3 |  | 0
2.9.7 | Refrigerant charge - R410A (or as per unit selection) | sum | 1 |  | 0
2.9.8 | Nitrogen pressure test (≥40 bar holding for 24 hr) - certificate per circuit | no | 3 |  | 0
2.9.9 | Vacuum / dehydration to <500 microns including standing test | no | 3 |  | 0
2.9.10 | Commissioning report, signed | no | 3 |  | 0
2.9.11 | Additional item necessary for completion - contractor to describe |  |  |  | 0
2.9.12 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.9 - Testing & Commissioning |  |  | Subtotal | 0
2.10 | SPARES & RECOMMENDED CONSUMABLES
2.10.1 | Supplier to price on spares and consumables that susceptible to failure | sum | 1 |  | 0
2.10.2 | Supplier to submit list
2.10.3 | Additional item necessary for completion - contractor to describe |  |  |  | 0
| Subtotal 2.10 - Spares |  |  | Subtotal | 0
2.11 | ADDITIONAL ITEMS BY CONTRACTOR
Additional items NOT stipulated in this BoQ or the Specification (and vice versa) that are necessary for a complete, fully operational and balanced installation of the DX CRAC system. NOTE: Additional items may NOT be claimed at a later stage by the Contractor unless the design scope changes. Contractor to insert line items below with descriptions, units and quantities for tender clarity.
2.11.1 |  |  |  |  | 0
2.11.2 |  |  |  |  | 0
2.11.3 |  |  |  |  | 0
2.11.4 |  |  |  |  | 0
2.11.5 |  |  |  |  | 0
2.11.6 |  |  |  |  | 0
2.11.7 |  |  |  |  | 0
2.11.8 |  |  |  |  | 0
| Subtotal 2.11 - Additional Items |  |  | Subtotal | 0
| BILL 2 - DX CRAC UNITS |  |  | SUB-TOTAL | 403774.682
Carried forward to Summary Page →

## DST - Scheme C
TECHNICAL DATA SHEET — CRAC UNIT (Direct Expansion) — SCHEME C (SCHNEIDER UNIFLAIR)
PROJECT: WITS - SMH DATA CENTRE ¦ SCHEME: C (SCHNEIDER UNIFLAIR) ¦ REVISION: 01 ¦ DATE: 22/05/2026
INSTRUCTIONS TO VENDOR
1 | Failure to complete this TDS will lead to reduced scoring in evaluation. A soft copy can be made available.
2 | Stamp or sign document when returning and include soft copy.
3 | VS = Vendor specification (vendor to complete). TBC = To be confirmed by consultant.
4 | CD column: Comply (comply in full) or Deviate (do not comply in full or at all — complete Offered cell with actual value).
5 | Complete the "CD" and "Offered" columns for every row.
6 | Reason for Exception — confirm reason for deviation. Required for values that substantially differ from specified.
7 | A/R — Accept/Reject — Consultant acceptance/rejection of deviation or offer. Vendor: leave blank.
LEGEND: Yellow cells = Specified input ¦ Orange cells = Vendor to complete ¦ Green cells = Calculated values
# | DESCRIPTION | UNIT | SPECIFIED | OFFERED | CD | REASON FOR EXCEPTION | A/R
GENERAL
1 | Equipment reference | - | SMH-CRAC-06/07/08
2 | Vendor | -
3 | Manufacturer | -
4 | Model number / series | -
5 | Country of origin | -
6 | Location / site | - | Johannesburg
7 | Number of units (Day 1 / Final) | # | 3
8 | Equipment tag numbers | - | See Dwg
9 | Warranty period | Yrs | 1
10 | Unit type | - | CRAC - Downblow
11 | Redundancy configuration | - | N/A
1. ENVIRONMENTAL
1 | Site altitude | masl | 1750
2 | Air pressure at altitude (calculated) | kPa | 81.994
3 | Air density at altitude (calculated) | kg/m³ | 0.95803
4 | Design outdoor dry-bulb temperature (summer) | °C | 37
5 | Design outdoor wet-bulb temperature (summer) | °C | 21.9
6 | Design outdoor dry-bulb temperature (winter) | °C | 1.6
7 | Environmental corrosivity category (ISO 12944) | - | C2 - Low
8 | IP rating — indoor unit (IEC 60529) | IP | IP20
9 | IP rating — outdoor unit (IEC 60529) | IP | IP65
10 | Noise: Lp sound pressure level @ 2 m (ISO 3744) | dBA | <70
11 | Selection derated for site conditions (altitude, ambient)? | Y/N | Yes
12 | Seismic zone classification (if applicable) | - | N/A
2. FILTRATION
1 | Filter class — dry media (EN 779 / ISO 16890) | - | G4 / ePM10 ≥50%
2 | Filter type / media | - | Pleated panel
3 | Additional filters (1 set for commissioning) | Y/N | Yes
4 | HEPA / carbon pre-filter option | Y/N | No
3. PERFORMANCE — DIRECT EXPANSION (DX)
1 | Refrigerant type | - | R410A
2 | Refrigerant safety group (ISO 817 / ASHRAE 34) | - | A1
3 | Refrigerant GWP (AR5) | - | 2088
4 | Refrigerant charge per circuit | kg | VS
5 | Number of refrigerant circuits | # | 2
6 | Number of compressors per circuit | # | 1
7 | Compressor type | - | Inverter Scroll
8 | Net design sensible cooling capacity (at EN 14511) | kWth | 58.6
9 | Total design cooling capacity (incl. fan load) | kWth | VS
10 | Total sensible cooling capacity (incl. fan load) | kWth | VS
11 | Sensible heat ratio (SHR) | - | ≥0.90
12 | Unit inlet air temperature (return air) | °C | 34
13 | Off-coil temperature | °C | 20
14 | Design delta T over unit (calculated) | °C | 14
15 | Unit inlet air relative humidity | % | 26.3
16 | Cooling efficiency (Total cooling / Total power) — EER | kWth/kW_e | ≥3.5
17 | Unit specific fan power SFP | W/(m³/h) | <0.25
18 | Part load performance (50% load EER) | kWth/kW_e | VS
19 | Compressor power consumption at design | kW_e | VS
20 | Total unit power consumption at design | kW_e | VS
4. FAN & AIRFLOW MANAGEMENT — INDOOR UNIT
1 | Fan type | - | EC
2 | Airflow direction | - | Down blow, top return
3 | Containment type | - | Cold aisle
4 | Airflow (design) | m³/s | 4.3474
5 | Airflow velocity over coil | m/s | ≤2.5
6 | Number of fans | # | VS
7 | External static pressure (ESP) | Pa | 80
8 | Total pressure drop incl. ESP | Pa | VS
9 | Fan motor efficiency (IE class) | - | IE4 minimum
10 | Fan nominal unit power consumption | kW_e | VS
11 | Fan rated power consumption at selection | kW_e | VS
12 | Fan rated absorbed current at selection | A | VS
13 | Fan speed control | - | Variable (0–100%)
5. FAN & AIRFLOW MANAGEMENT — OUTDOOR UNIT
1 | Fan type | - | EC
2 | Air discharge direction | - | VS
3 | Fan rated absorbed current at selection | A | VS
4 | Fan rated power consumption at selection | kW_e | VS
5 | Number of condenser fans | # | VS
6 | Condenser coil face area | m² | VS
7 | Condenser airflow | m³/s | VS
6. COIL & FITTINGS
1 | Dual coil | Y/N | No
2 | Evaporator coil material | - | Cu/Al
3 | Coil coating / corrosion protection | - | Epoxy or equivalent
4 | Number of rows (evaporator) | # | VS
5 | Fin spacing | FPI | VS
6 | Expansion valve type | - | EEV (Electronic)
7 | Expansion valve / connection size | mm | VS
8 | Condensate tray material | - | SS
7. CONDENSATE PIPING & DRAINAGE
1 | Condensate drain connection size (unit stub) | mm | VS
2 | Condensate pipe material | - | uPVC
3 | Condensate drainage method | - | Gravity
4 | Condensate pump required | Y/N | No
5 | Condensate pump head (if pumped) | m | N/A
6 | Condensate pump capacity | l/hr | N/A
7 | Condensate pipe minimum gradient (gravity) | - | 1:100 (1%)
8 | P-trap / U-bend on drain connection | Y/N | Yes
9 | P-trap depth minimum | mm | 50
10 | Condensate drain to be insulated (to prevent sweating) | Y/N | Yes
11 | Condensate drain insulation material | - | Closed-cell elastomeric
12 | Condensate overflow alarm / float switch | Y/N | Yes
13 | Condensate drain termination | - | To building drain or sump
14 | Estimated condensate rate per unit at design conditions | l/hr | VS
Note: All condensate piping to be installed with minimum fall to prevent standing water. Insulation required below raised floor.
8. ELECTRICAL
1 | Voltage / phase / frequency | V/Ph/Hz | 400 / 3 / 50
2 | Power feed configuration | - | Dual (A/B)
3 | ATS fitted | Y/N | Yes
4 | ATS transfer time | ms | ≤20
5 | Controller power source installed after ATS (no break on loss of stream) | Y/N | Yes
6 | Supercapacitor / UPS to controls | Y/N | Yes
7 | Supercapacitor ride-through time | min | ≥5
8 | Total unit full load current (FLC) | A | VS
9 | Total unit maximum current (locked rotor / inrush) | A | VS
10 | Unit power factor at design load | - | VS
11 | Main circuit breaker rating (indoor unit) | A | VS
12 | Recommended upstream MCCB / fuse rating | A | VS
13 | Cable entry size (gland plate) | mm | VS
14 | Earth leakage / RCD requirement | Y/N | VS
15 | Harmonic distortion (THDi) at full load | % | <10%
9. CONFIGURATION OPTIONS
1 | Unit type | - | CRAC
2 | Pipework connection (top / side / bottom) | - | Bottom
3 | Dehumidification cycle | Y/N | Yes
4 | Free cooling / economiser mode | Y/N | No
5 | Free cooling activation temperature | °C | N/A
6 | Hot gas bypass | Y/N | No
7 | Soft start / inverter on compressor | Y/N | VS
10. PROTECTION AND SAFETY FEATURES
1 | Fire classification including all parts (EN 13501-1) | - | B
2 | Fire shutdown from external input (volt-free contact) | Y/N | No
3 | High pressure cutout | Y/N | Yes
4 | Low pressure cutout | Y/N | Yes
5 | Compressor overtemperature protection | Y/N | Yes
6 | Anti-short-cycle timer | Y/N | Yes
7 | Phase protection (loss / reversal / imbalance) | Y/N | Yes
8 | Refrigerant leak detection onboard | Y/N | Yes
9 | Leak detection sensor type | - | Infrared / semiconductor
10 | Safety valve per SANS 10147:2014 / EN 378 | Y/N | VS
11. TESTING AND CERTIFICATIONS
1 | Factory acceptance testing (FAT) required | Y/N | No
2 | Certifications — safety, performance, labelling | - | EN 14511
3 | Electrical safety compliance to EN/IEC 60204 | Y/N | Yes
4 | Electrical compliance to IEC/EN 60947-1 (circuit breakers) | Y/N | Yes
5 | Standard product marking | - | UL, CE, IEC — indicate other
6 | ASHRAE 127 performance testing | Y/N | VS
7 | Pressure vessel registration (if applicable) | Y/N | VS
12. CONTROLS AND MONITORING
1 | HMI panel (touch screen) | Y/N | Yes
2 | HMI display size (minimum) | inch | ≥5
3 | Remote monitoring ability | Y/N | Yes
4 | Primary communication protocol | - | BACnet IP
5 | Secondary communication protocol | - | Modbus RTU
6 | SNMP support (v2c / v3) | Y/N | Yes
7 | Dry contact inputs (volt-free) | # | ≥4
8 | Dry contact outputs (alarm relay) | # | ≥2
9 | Master/slave capability (multi-unit coordination) | Y/N | Yes
10 | Maximum units in master/slave group | # | ≥5
11 | Temperature control method | - | Off coil temp
12 | Fan speed control method | dP / dT | dT
13 | Supply of differential pressure sensors (installation by others) | Y/N | No
14 | Filter ΔP monitoring for dirty filter alarm | Y/N | Yes
15 | Remote analog sensor inputs (RH / temp / dP) — min 5 | Y/N | Yes
16 | Onboard event / alarm logging (min 500 events) | Y/N | Yes
17 | Web browser interface for local access | Y/N | VS
18 | Ethernet port (RJ45) | # | ≥1
13. COMMUNICATION PROTOCOL DETAIL
1 | BACnet — BACnet/IP support | Y/N | Yes
2 | BACnet — BACnet MS/TP support | Y/N | VS
3 | BACnet — PICS (Protocol Implementation Conformance Statement) provided | Y/N | Yes
4 | BACnet — BTL listed | Y/N | VS
5 | BACnet — Supported objects (AV, AI, AO, BV, BI, BO) | - | VS
6 | Modbus — Modbus RTU (RS485) support | Y/N | Yes
7 | Modbus — Modbus TCP/IP support | Y/N | VS
8 | Modbus — Register map / points list provided | Y/N | Yes
9 | SNMP — MIB file provided | Y/N | VS
10 | SNMP — Trap destination configurable | Y/N | VS
11 | Points list / integration guide provided with submission | Y/N | Yes
12 | Network interface — 10/100/1000 Base-T | Y/N | Yes
14. HEATER REQUIREMENT (WINTER REHEAT)
Heater required when return air absolute humidity>10.75g/kg and the unit has to dehumidify to the upper absolute humidity and overcools below supply air
1 | CRAC temperature setpoint | °C | 20
2 | Minimum acceptable supply air temperature | °C | 15
3 | Design airflow (from Section 4) | m³/s | 4.3474
4 | Air density at altitude (from Section 1) | kg/m³ | 0.95803
5 | Reheat duty required: Q = ρ × V̇ × Cp × (T_room - T_min_supply) | kW | 20.9286
6 | Heater type | - | PTC electric
7 | Heater capacity (vendor to confirm ≥ calculated) | kW | VS
8 | Heater stages | # | VS
9 | Heater safety cutout temperature | °C | VS
10 | Heater required | Y/N | Yes
15. HUMIDIFIER REQUIREMENT
Humidifier required when return air humidity drops below setpoint. Sized for worst-case winter infiltration / make-up air scenario.
1 | Room RH setpoint (minimum) | % | 12.1
2 | Winter outdoor air moisture content (approximate) | g/kg | 1.31
3 | Room air moisture content at setpoint | g/kg | 2.4
4 | Estimated infiltration / make-up air rate | m³/s | 0.15
5 | Air density (from Section 1) | kg/m³ | 0.95803
6 | Moisture deficit: Δω = ω_room - ω_outdoor | g/kg | 1.09
7 | Humidification load: ṁ_w = ρ × V̇_infil × Δω / 1000 | kg/hr | 0.56389
8 | Humidification electrical load (electrode: ~0.75 kW per kg/hr) | kW | 0.42292
9 | Humidifier type | - | Adiabatic Humidifier
10 | Humidifier capacity (vendor to confirm ≥ calculated) | kg/hr | VS
11 | Humidifier water quality requirement | - | Potable — confirm conductivity range
12 | Humidifier water supply connection size | mm | VS
13 | Humidifier drain connection size | mm | VS
14 | Humidifier steam distribution lance in duct / plenum | Y/N | VS
15 | Humidifier required | Y/N | Yes
16. DIMENSIONS, ACCESS, FITTINGS & FINISHING — INDOOR UNIT
1 | Height (excl. fan box) | mm | 986
2 | Width | mm | 3660
3 | Depth | mm | 920
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | VS
6 | Minimum maintenance clearance — front | mm | VS
7 | Minimum maintenance clearance — rear | mm | VS
8 | Material of manufacture (casing) | - | Powder-coated galvanised steel
9 | Cable entries | - | Bottom
10 | Raised floor installation | Y/N | No
11 | Raised floor tile cutout dimensions (W × D) | mm | VS
12 | Vibration isolation (anti-vibration mounts) | Y/N | Yes
13 | Colour and finish | - | RAL 7035 or supplier standard
14 | All piping inside unit factory insulated | Y/N | Yes
17. DIMENSIONS, ACCESS, FITTINGS & FINISHING — OUTDOOR UNIT
1 | Height | mm | 1980
2 | Width | mm | 1750
3 | Depth | mm | 890
4 | Total mass (operating weight) | kg | VS
5 | Maintenance and access requirements | - | Front
6 | Minimum maintenance clearance | mm | VS
7 | Material of manufacture (casing) | - | Powder-coated galvanised steel
8 | Cable entries | - | Bottom
9 | Vibration isolation | Y/N | Yes
10 | Colour and finish | - | RAL 7035 or supplier standard
11 | All piping inside unit factory insulated | Y/N | Yes
12 | Hail guards fitted | Y/N | Yes
13 | Maximum refrigerant pipe run (IDU to ODU) | m | VS
14 | Maximum elevation difference (IDU to ODU) | m | VS
18. REFRIGERANT PIPING
1 | Suction line connection size (IDU) | mm OD | VS
2 | Liquid line connection size (IDU) | mm OD | VS
3 | Suction line connection size (ODU) | mm OD | VS
4 | Liquid line connection size (ODU) | mm OD | VS
5 | Connection type (flare / braze / Victaulic) | - | Braze
6 | Factory-charged (confirm refrigerant piping length) | Y/N | VS
7 | Additional refrigerant charge per metre of pipe | g/m | VS
8 | Pipe insulation — suction line | - | As per manufacturer recommendation
9 | Pipe insulation — liquid line | - | As per manufacturer recommendation
10 | Oil return provisions for long pipe runs | Y/N | VS
11 | Nitrogen pressure test pressure | bar | VS
19. OPTIONS AND ACCESSORIES
1 | Rapid restart after power loss | Y/N | Yes
2 | Heater (see Section 14 for sizing) | Y/N | Yes
3 | Humidifier (see Section 15 for sizing) | Y/N | Yes
4 | Under-floor water leak detection rope / sensor | Y/N | Yes
5 | Drip tray under unit (full footprint) | Y/N | No
6 | Smoke detector input | Y/N | Yes
7 | Caster wheels for positioning | Y/N | VS
8 | Louvred floor tile(s) supplied | Y/N | VS
9 | Remote condenser controller | Y/N | VS
20. RECOMMENDED SPARE PARTS
1 | Spare filter set (per unit) | # | 1
2 | Spare fan assembly | # | 1
3 | Spare compressor | # | VS
4 | Spare expansion valve | # | 1
5 | Spare controller / PCB | # | 1
6 | Spare humidifier cylinder (if fitted) | # | 1
7 | Spare drive belts (if applicable) | # | VS
8 | Spare fuses / MCBs | set | 1
9 | Manufacturer recommended 2-year spares list provided | Y/N | Yes
21. PRODUCTION AND DELIVERY
1 | Lead time for factory production | Wk | VS
2 | Lead time for delivery kerbside | Wk | VS
3 | Delivery method (shipping / road) | - | VS
4 | Packaging suitable for forklift / crane handling | Y/N | VS
5 | Commissioning support by manufacturer (on-site) | Y/N | Yes
6 | Training provided (O&M staff) | Y/N | Yes
7 | Extended warranty option available | Y/N | VS
22. DOCUMENTATION DELIVERABLES
1 | Equipment data sheet / product selection printout | Y/N | Yes
2 | Certified dimensional drawings (DXF / PDF) | Y/N | Yes
3 | Wiring diagram / electrical schematic | Y/N | Yes
4 | Refrigerant piping diagram (P&ID) | Y/N | Yes
5 | BACnet / Modbus points list | Y/N | Yes
6 | SNMP MIB file (if SNMP supported) | Y/N | VS
7 | Installation, operation & maintenance manual | Y/N | Yes
8 | Noise level test certificate (ISO 3744) | Y/N | Yes
9 | Performance test certificate (EN 14511) | Y/N | Yes
10 | Refrigerant safety data sheet (SDS) | Y/N | Yes
23. FURTHER CLARIFICATION
1 |  | -
2 |  | -
3 |  | -
4 |  | -
5 |  | -
6 |  | -
7 |  | -
8 |  | -
9 |  | -
10 |  | -
NOTES
1 | All units are to be installed according to the manufacturer's requirements including maintenance access clearances.
2 | Manufacturer's recommended minimum spares are to be supplied.
3 | All items that deviate from standard supply to be brought to the attention of the Owner.
4 | All calculations are based on Johannesburg site conditions (1695 masl). Vendor to confirm selection is derated accordingly.
5 | Condensate piping specification applies from the unit drain stub to the nearest building drain point.
6 | Communication protocol points lists must be submitted with the tender response for BMS integration review.
7 | Heater and humidifier sizing is indicative — vendor to confirm capacity meets or exceeds calculated values.
8 | All refrigerant piping between IDU and ODU to be by specialist refrigeration contractor to manufacturer's specification.
9 | Vendor to confirm compliance with SANS 10147:2014 for pressure equipment and EN 378 for refrigeration safety.